## Checklist
sequence | content | assignee_email | start_date | end_date | estimated_hours | status
1 | [Smartrack/PTU docs] Audit dokumen Smartrack dan PTU lama terhadap Rivew Dokument Protocol Output.pdf; buat matrix perubahan per temuan review dan source config/MIB aktif. | dedenh842@gmail.com | 2026-08-21 | 2026-08-21 | 3 | not_started
2 | [Smartrack/PTU docs] Perbarui format dan branding Smartrack/PTU mengikuti contoh dokumentasi manual user yang telah diberikan kepada Deden dan Ikhsal: logo resolusi tinggi, nomor dokumen, cover, revision scheme, approver/reviewer, confidentiality, footer, document control, revision history, scope, source/version, dan release status. | dedenh842@gmail.com | 2026-08-21 | 2026-08-21 | 3 | not_started
3 | [Smartrack/PTU docs] Tambahkan penjelasan OID segmentation: GSPE .10, Smartrack .10.14, PTU .10.15, Container .10.16; jelaskan section, device-instance/subsection, parameter, dan scalar .0. | ikhsalg@gmail.com | 2026-08-21 | 2026-08-21 | 3 | not_started
4 | [Smartrack/PTU docs] Migrasikan PTU dari .10.14 ke .10.15 sesuai keputusan product owner; regenerasi seed, runtime JSON, MIB, export, dan dokumentasi. Pastikan Smartrack tetap .10.14 dan tidak ada collision antarproduk. | ikhsalg@gmail.com | 2026-08-21 | 2026-08-21 | 5 | not_started
5 | [Smartrack/PTU docs] Tambahkan kolom access READ ONLY/READ-WRITE, type, scale/unit, enum/status mapping, source topic/register/OID, dan validation evidence ke register map Smartrack/PTU dari source config/library. | dedenh842@gmail.com | 2026-08-24 | 2026-08-24 | 5 | not_started
6 | [Smartrack/PTU docs] Dokumentasikan semua form Protocol Config UI Smartrack/PTU beserta screenshot: communication, section, subsection, parameter, import/export, validation state. | dedenh842@gmail.com | 2026-08-24 | 2026-08-24 | 3 | not_started
7 | [Smartrack/PTU docs] Ambil screenshot polling input dan SNMP GET/WALK untuk Smartrack/PTU; sertakan protocol version, command, timestamp, firmware/config version, dan hasil. | ikhsalg@gmail.com | 2026-08-24 | 2026-08-24 | 4 | not_started
8 | [Smartrack/PTU docs] Generate dan review ulang dokumen Smartrack dan PTU; verifikasi register source, OID prefix, access, screenshot, serta pagination sebelum release. | dedenh842@gmail.com | 2026-08-24 | 2026-08-24 | 4 | not_started
9 | [Baseline] Tegaskan Device Library sebagai single source of truth protocol input. Dilarang membuat variable, type, scale, register, OID, enum, atau access baru di protocol output. Jika device/part number tidak diketahui atau tidak memiliki exact match, hentikan mapping device tersebut dan konfirmasi ke Juarendra sebelum perubahan library. | dedenh842@gmail.com | 2026-08-25 | 2026-08-25 | 1.5 | not_started
10 | [Baseline] Tetapkan dua deployment terpisah untuk Container 20 ft dan 40 ft. Keduanya memakai OID product base .1.3.6.1.4.1.10000.10.16 dan tidak dijalankan bersamaan pada satu SNMP agent. | ikhsalg@gmail.com | 2026-08-25 | 2026-08-25 | 1 | not_started
11 | [Library audit] Export snapshot versioned dari apps/container/app/backend/data/library/modbus/devices.json dan modular/devices.json; catat commit SHA dan checksum. | dedenh842@gmail.com | 2026-08-25 | 2026-08-25 | 1 | not_started
12 | [Library audit] Cocokkan setiap equipment 20 ft dan 40 ft dengan manufacturer, part_number, protocol, category, dan selectedDevice Device Library. | dedenh842@gmail.com | 2026-08-25 | 2026-08-25 | 4 | not_started
13 | [Library audit] Buat gap list untuk equipment yang belum ada exact match di Device Library. Konfirmasi model/mapping ke Juarendra (juanrendra@gspe.co.id); setelah disetujui, tambah/fix Device Library lebih dahulu, bukan protocol output. Simpan keputusan sebagai evidence. | dedenh842@gmail.com | 2026-08-26 | 2026-08-26 | 3 | not_started
14 | [Container 20 ft] Validasi konfigurasi Container 20 ft yang sudah ada: 13 SHT40, 1 FS3000-1005, 1 SDP810-125, 5 AP8881, 2 ACRD301P, 2 PM5650, TA63D4L4004TPE, EMUPS50K250QBHS. | dedenh842@gmail.com | 2026-08-26 | 2026-08-26 | 3 | not_started
15 | [Container 20 ft] Lengkapi instance 20 ft yang belum terdaftar: SPS30, LIS3DHTR, water leak/dry contact, human presence, gas, battery cabinet, access/CCTV, dan relay sesuai Device Library/module yang benar. | dedenh842@gmail.com | 2026-08-26 | 2026-08-26 | 4 | not_started
16 | [Container 40 ft] Map tiap equipment 40 ft ke entri Device Library exact. Pertahankan source protocol/IP/Modbus address/topic dari daftar instalasi; jangan salin variable dari part number yang mirip. | dedenh842@gmail.com | 2026-08-26 | 2026-08-26 | 5 | not_started
17 | [Container 40 ft] Pertahankan seluruh inventory 40 ft sesuai file list, termasuk Power Meter 2 M4M mati, ATS022 optional, Palm Vein on progress, dan device tanpa topic. Catat readiness/status aktual tanpa menghapus item dari scope; konfirmasi mapping yang tidak diketahui ke Juarendra. | dedenh842@gmail.com | 2026-08-27 | 2026-08-27 | 2 | not_started
18 | [Input test] Polling setiap device melalui protocol input. Verifikasi seluruh variable Device Library muncul pada MQTT payload dengan nama dan value yang sama. | dedenh842@gmail.com | 2026-08-27 | 2026-08-27 | 6 | not_started
19 | [Input test] Validasi type, relative_address/OID, register_type, word_length, multiplier, table index, dan write_access terhadap hasil polling; perbaiki Device Library bila mismatch. | dedenh842@gmail.com | 2026-08-27 | 2026-08-27 | 5 | not_started
20 | [Input test] Uji nilai normal, alarm, missing device, timeout, malformed payload, dan restart. Variable yang tidak dipublish tidak boleh diekspor. Handover inventory tervalidasi ke Ikhsal. | dedenh842@gmail.com | 2026-08-27 | 2026-08-27 | 4 | not_started
21 | [Container 20 ft] Generate protocol output config profil 20 ft dari inventory Device Library tervalidasi: .10.16 > section > device instance > variable. Pertahankan variable name literal dari library. | ikhsalg@gmail.com | 2026-08-28 | 2026-08-28 | 4 | not_started
22 | [Container 40 ft] Generate protocol output config profil 40 ft dari inventory Device Library tervalidasi: .10.16 > section > device instance > variable. Pertahankan variable name literal dari library. | ikhsalg@gmail.com | 2026-08-28 | 2026-08-28 | 4 | not_started
23 | [Output config] Set seluruh SNMP dan Modbus TCP protocol output READ ONLY. READ/WRITE hanya diizinkan untuk output Modular Mini Relay dan Relay dengan command acknowledgement, interlock, timeout, dan FAT. | ikhsalg@gmail.com | 2026-08-28 | 2026-08-28 | 3 | not_started
24 | [Output config] Generate MIB, SNMP runtime JSON, Modbus register map, dan register document dari satu source config. Pastikan OID unik, Modbus address/endian stabil, dan overlap ditolak. | ikhsalg@gmail.com | 2026-08-28 | 2026-08-28 | 6 | not_started
25 | [UI] Tampilkan Device Library source, selectedDevice, source protocol, variable, input register/OID, multiplier, access, dan output OID pada Protocol Config UI sebagai read-only traceability. | ikhsalg@gmail.com | 2026-08-31 | 2026-08-31 | 3 | not_started
26 | [Deploy] Set PRODUCT_NAME=container, persist SNMP/Modbus TCP config per profile, bind Modbus port/ACL, dan pastikan tidak fallback ke Smartrack. | ikhsalg@gmail.com | 2026-08-31 | 2026-08-31 | 4 | not_started
27 | [QC] Bandingkan output SNMP GET/WALK dan Modbus TCP (termasuk decode address/type) dengan payload MQTT. Catat raw dan engineering value. | ikhsalg@gmail.com | 2026-08-31 | 2026-08-31 | 6 | not_started
28 | [QC] Uji SET/FC06/FC16: semua non-relay wajib ditolak. READ/WRITE hanya Modular Mini Relay dan Relay dengan type/range validation, interlock, exception handling, timeout, read-back, dan audit. | ikhsalg@gmail.com | 2026-08-31 | 2026-08-31 | 5 | not_started
29 | [Container docs] Generate dokumen protocol output final Container 20 ft dari Device Library snapshot. Sertakan cover manual user, commit SHA, mapping device, source register/OID, scale, access, topic, output OID, UI screenshot, dan polling evidence. | ikhsalg@gmail.com | 2026-09-01 | 2026-09-01 | 4 | not_started
30 | [Container docs] Generate dokumen protocol output final Container 40 ft dari Device Library snapshot. Sertakan cover manual user, commit SHA, mapping device, source register/OID, scale, access, topic, output OID, UI screenshot, dan polling evidence. | ikhsalg@gmail.com | 2026-09-01 | 2026-09-01 | 4 | not_started
31 | [Acceptance] Sign-off engineering: tidak ada variable manual; seluruh inventory pada list tetap tercatat; device tidak dikenal memiliki keputusan Juarendra; profile 20 ft/40 ft terpisah; semua non-relay READ ONLY; hanya Modular Mini Relay/Relay dapat ditulis; payload/SNMP evidence dan dokumen final tersedia. | ikhsalg@gmail.com | 2026-09-01 | 2026-09-01 | 3 | not_started

## 20ft Existing Mapping
Device Name | Manufacturer | Part Number | Selected Device | Category | MQTT Topic | Interval | Library Match | Library Variables | Execution Action
Panasonic Battery 1 | Panasonic | DCB105ZK | Panasonic-DCB105ZK | battery | IOT/Panasonic_Batt/1 | 10 | MATCH | serial_number, barcode, voltage, current, dc, fcc, rc, soc, soh, cycle_count, cell_1_voltage, cell_2_voltage, cell_3_voltage, cell_4_voltage, cell_5_voltage, cell_6_voltage, cell_7_voltage, cell_8_voltage, cell_9_voltage, cell_10_voltage, cell_11_voltage, cell_12_voltage, cell_13_voltage, status, warning, alarm, error | Use all library variables; validate MQTT payload
Drycontact 1 | IOT | DRYCONTACT | IOT-DRYCONTACT | Modular | IOT/DC/1 | 10 | GAP | - | Create/repair exact Device Library entry first
RELAY1 | IOT | RELAY | IOT-RELAY | Modular | IOT/RELAY/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Recti | DPC | SC501 | DPC-SC501 | rectifier | IOT/RECTI/DPC | 10 | MATCH | AC_Online_Status, Battery_State, Battery_voltage_current, Ambient Temperature, AC_Input_1_Voltage_Phase_A, AC_Input_1_Voltage_Phase_B, AC_Input_1_Voltage_Phase_C, AC_Input_2_Voltage_Phase_A, AC_Input_2_Voltage_Phase_B, AC_Input_2_Voltage_Phase_C, AC_Input_1_Current_Phase_A, AC_Input_1_Current_Phase_B, AC_Input_1_Current_Phase_C, AC_Input_2_Current_Phase_A, AC_Input_2_Current_Phase_B, AC_Input_2_Current_Phase_C, AC_Input_1_Active_Power_Phase_A, AC_Input_1_Active_Power_Phase_B, AC_Input_1_Active_Power_Phase_C, AC_Input_2_Active_Power_Phase_A, AC_Input_2_Active_Power_Phase_B, AC_Input_2_Active_Power_Phase_C, AC_Input_1_Reactive_Power_Phase_A, AC_Input_1_Reactive_Power_Phase_B, AC_Input_1_Reactive_Power_Phase_C, AC_Input_2_Reactive_Power_Phase_A, AC_Input_2_Reactive_Power_Phase_B, AC_Input_2_Reactive_Power_Phase_C, AC_Input_1_Apparent_Power_Phase_A, AC_Input_1_Apparent_Power_Phase_B, AC_Input_1_Apparent_Power_Phase_C, AC_Input_2_Apparent_Power_Phase_A, AC_Input_2_Apparent_Power_Phase_B, AC_Input_2_Apparent_Power_Phase_C, AC_Input_1_Active_Energy_Phase_A, AC_Input_1_Active_Energy_Phase_B, AC_Input_1_Active_Energy_Phase_C, AC_Input_2_Active_Energy_Phase_A, AC_Input_2_Active_Energy_Phase_B, AC_Input_2_Active_Energy_Phase_C, AC_Input_1_Reactive_Energy_Phase_A, AC_Input_1_Reactive_Energy_Phase_B, AC_Input_1_Reactive_Energy_Phase_C, AC_Input_2_Reactive_Energy_Phase_A, AC_Input_2_Reactive_Energy_Phase_B, AC_Input_2_Reactive_Energy_Phase_C, AC_Input_1_Apparent_Energy_Phase_A, AC_Input_1_Apparent_Energy_Phase_B, AC_Input_1_Apparent_Energy_Phase_C, AC_Input_2_Apparent_Energy_Phase_A, AC_Input_2_Apparent_Energy_Phase_B, AC_Input_2_Apparent_Energy_Phase_C, AC_Input_1_Frequency_Phase_A, AC_Input_1_Frequency_Phase_B, AC_Input_1_Frequency_Phase_C, AC_Input_2_Frequency_Energy_Phase_A, AC_Input_2_Frequency_Phase_B, AC_Input_2_Frequency_Phase_C, AC_Input_1_Last_Month_Energy, AC_Input_1_Curent_Month_Energy, AC_Input_2_Last_Month_Energy, AC_Input_2_Curent_Month_Energy, Number_of_Installed_Rectifiers, Number_of_Fault_Rectifier, Load_Rate, Output_Current_of_Rectifiers, Type_Rectifier, Vin, Vout, Output_Current, Ambient_Temperature, Primary_Hot_Temperature, Secondary_Hot_Temperature, Out_Current_Limit, Number_of_branches, Bus_Voltage, DC_Energy, Load_Current, Battery_Status, Battery_1_Capacity, Battery_2_Capacity, Battery_3_Capacity, Battery_4_Capacity, Battery_5_Capacity, Battery_6_Capacity, Battery_7_Capacity, Battery_8_Capacity, Voltage(BMS), Current(BMS), Cycle_Counts(BMS), Total_Capacity(BMS), SOC(BMS), SOH(BMS), Ambient_Temperature(BMS), Maximum_Voltage(BMS), Minimum_Voltage(BMS), Average_Voltage(BMS), Temperature_Batt_1, Temperature_Batt_2, EX-Temperature_1, EX-Temperature_2, Amb_Temperature, Humidity, AC_Alarm_1, DC_Alarm_1, DC_Total_Load_Slight_Over_Current, DC_Total_Load_Severe_Over_Current, System_SPD_Fault, System_Total_Alarm, BMS1_communication_fault, Temperature_sensor_1_not_assemble, Temperature_sensor_2_not_assemble, EX-Temperature_sensor_1_not_assemble, EX-Temperature_sensor_2_not_assemble, LLVD_Alarm, BLVD_Alarm, LLVD1_Fail, LLVD2_Fail, LLVD3_Fail, LLVD4_Fail, LLVD5_Fail, LLVD6_Fail, LLVD7_Fail, LLVD8_Fail, BLVD_Fail, PreAlarm-LLVD1, PreAlarm-LLVD2, PreAlarm-LLVD3, PreAlarm-LLVD4, PreAlarm-LLVD5, PreAlarm-LLVD6, PreAlarm-LLVD7, PreAlarm-LLVD8, PreAlarm-BLVD, Battery_Break, Ambient_High1_Temperature, Ambient_High2_Temperature, Battery_Charge_Over_current, Battery_Discharge, Battery_Cycle_Test_Over_current, Battery_Middle_Imbalance, Battery_Can_Not_Charge, DC_Branch_Slight_Over_Current, DC_Branch_Severe_Over_Current, Load_Break, Load_Break_, Ambient_Temperature_Low1, Ambient_Temperature_Low2, Humidity_High, Humidity_Low, Battery_Temperature_High1, Battery_Temperature_High2, Battery_Temperature_Low1, Battery_Temperature_Low2, BTRM_High_1, BTRM_High_2, AC_System_Alarm, DC_System_Alarm | Use all library variables; validate MQTT payload
PH1 | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph1 | 10 | GAP | - | Create/repair exact Device Library entry first
PH2 | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph2 | 10 | GAP | - | Create/repair exact Device Library entry first
PH3 | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph3 | 10 | GAP | - | Create/repair exact Device Library entry first
Sensor Temp Hum 1 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_1 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
Rack PDU 1 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_1 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 2 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_2 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 3 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_3 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 4 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_4 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 5 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_5 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 6 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_6 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 7 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_7 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 8 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_8 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 9 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_9 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 10 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_10 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
RACK PDU 11 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | container/rpdu/rpdu_11 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 2 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_2 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 3 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_3 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 4 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_4 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 5 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_5 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 6 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_6 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 7 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_7 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 8 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_8 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 9 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_9 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 10 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_10 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 11 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_11 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 12 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_12 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 13 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_13 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 14 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_14 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 15 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_15 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 16 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_16 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 17 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_17 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 18 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_18 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 19 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_19 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 20 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_20 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 21 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_21 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM 22 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | container/temphum/temp_hum_22 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
COOLING 1 C | VNCool | VR012 | VNCool-VR012 | aircond | container/cooling/cooling_1 | 10 | MATCH | Return_Air_Temperature, Return_Air_Humidity, Supply_Air_Temperature_1, Supply_Air_Temperature_2, Exhaust_Pressure, Suction_Pressure, Exhaust_Temperature, Suction_Temperature, Alarm_1, Alarm_2, Alarm_3, Unit_Mode, Unit_Operation_Status, Remote_Temperature_1, Remote_Temperature_2, Remote_Temperature_3, Remote_Temperature_4, Remote_Temperature_5, Remote_Temperature_6, Remote_Temperature_7, Remote_Temperature_8, Remote_Temperature_9, Remote_Temperature_10, Remote_Temperature_11, Remote_Temperature_12, Remote_Temperature_13, Remote_Temperature_14, Remote_Temperature_15, Remote_Temperature_16, Supply_Air_Remote_Temperature_Set_Point, Return_Air_Temperature_Set_Point, Humidity_Set_Point, Monitoring_Switch, Suction_Superheat, Exhaust_Superheat, Compressor_Speed, EEV_Opening, Fan_Speed, Humidification_Current, Unit_Status, Alarm_4, Alarm_5, Alarm_6 | Use all library variables; validate MQTT payload
POWER METER 1 C | ABB | M4M30 | ABB-M4M30 | power_meter | container/power_meter/power_meter_1 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
COOLING 2 C | VNCool | VR012 | VNCool-VR012 | aircond | container/cooling/cooling_2 | 10 | MATCH | Return_Air_Temperature, Return_Air_Humidity, Supply_Air_Temperature_1, Supply_Air_Temperature_2, Exhaust_Pressure, Suction_Pressure, Exhaust_Temperature, Suction_Temperature, Alarm_1, Alarm_2, Alarm_3, Unit_Mode, Unit_Operation_Status, Remote_Temperature_1, Remote_Temperature_2, Remote_Temperature_3, Remote_Temperature_4, Remote_Temperature_5, Remote_Temperature_6, Remote_Temperature_7, Remote_Temperature_8, Remote_Temperature_9, Remote_Temperature_10, Remote_Temperature_11, Remote_Temperature_12, Remote_Temperature_13, Remote_Temperature_14, Remote_Temperature_15, Remote_Temperature_16, Supply_Air_Remote_Temperature_Set_Point, Return_Air_Temperature_Set_Point, Humidity_Set_Point, Monitoring_Switch, Suction_Superheat, Exhaust_Superheat, Compressor_Speed, EEV_Opening, Fan_Speed, Humidification_Current, Unit_Status, Alarm_4, Alarm_5, Alarm_6 | Use all library variables; validate MQTT payload
POWER METER 2 C | ABB | M4M30 | ABB-M4M30 | power_meter | container/power_meter/power_meter_2 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
POWER METE 3 C | ABB | M4M30 | ABB-M4M30 | power_meter | container/power_meter/power_meter_3 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
SENSOR VIBRATION 1 C | IOT | Vibration_Sensor | IOT-Vibration_Sensor | Sensor_RS485 | container/sensor/vibration_1 | 10 | MATCH | x, y, z, activity | Use all library variables; validate MQTT payload
SENSOR AIR PRESSURE 1 C | IOT | AirPressure_Sensor | IOT-AirPressure_Sensor | Sensor_RS485 | container/sensor/air_pressure_1 | 10 | MATCH | positif_pressure, negatif_pressure, temperature_in_line_pressure | Use all library variables; validate MQTT payload
SENSOR AIR FLOW 1 C | IOT | AirFlow_Sensor | IOT-AirFlow_Sensor | Sensor_RS485 | container/sensor/air_flow_1 | 10 | MATCH | airlow | Use all library variables; validate MQTT payload
SENSOR AIR QUALITY 1 C | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | container/sensor/air_quality_1 | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
SENSOR WATER LEAK 1 C | IOT | Water_Leak_Sensor | IOT-Water_Leak_Sensor | Sensor_RS485 | container/sensor/water_leak_1 | 10 | MATCH | water_leak | Use all library variables; validate MQTT payload
RACK PDU SR 1 C | Tripplite | PDUMNH32HV | Tripplite-PDUMNH32HV | pdu | smartrack/rpdu/rpdu_1 | 10 | MATCH | inlet_voltage, output_voltage, output_current_1, output_current_2 | Use all library variables; validate MQTT payload
COOLING SR 1 C | VNCool | VR012 | VNCool-VR012 | aircond | smartrack/cooling/cooling_1 | 10 | MATCH | Return_Air_Temperature, Return_Air_Humidity, Supply_Air_Temperature_1, Supply_Air_Temperature_2, Exhaust_Pressure, Suction_Pressure, Exhaust_Temperature, Suction_Temperature, Alarm_1, Alarm_2, Alarm_3, Unit_Mode, Unit_Operation_Status, Remote_Temperature_1, Remote_Temperature_2, Remote_Temperature_3, Remote_Temperature_4, Remote_Temperature_5, Remote_Temperature_6, Remote_Temperature_7, Remote_Temperature_8, Remote_Temperature_9, Remote_Temperature_10, Remote_Temperature_11, Remote_Temperature_12, Remote_Temperature_13, Remote_Temperature_14, Remote_Temperature_15, Remote_Temperature_16, Supply_Air_Remote_Temperature_Set_Point, Return_Air_Temperature_Set_Point, Humidity_Set_Point, Monitoring_Switch, Suction_Superheat, Exhaust_Superheat, Compressor_Speed, EEV_Opening, Fan_Speed, Humidification_Current, Unit_Status, Alarm_4, Alarm_5, Alarm_6 | Use all library variables; validate MQTT payload
SENSOR VIBRATION SR 1 C | IOT | Vibration_Sensor | IOT-Vibration_Sensor | Sensor_RS485 | smartrack/sensor/vibration_1 | 10 | MATCH | x, y, z, activity | Use all library variables; validate MQTT payload
SENSOR AIR PRESSURE SR 1 C | IOT | AirPressure_Sensor | IOT-AirPressure_Sensor | Sensor_RS485 | smartrack/sensor/air_pressure_1 | 10 | MATCH | positif_pressure, negatif_pressure, temperature_in_line_pressure | Use all library variables; validate MQTT payload
SENSOR AIR FLOW SR 1 C | IOT | AirFlow_Sensor | IOT-AirFlow_Sensor | Sensor_RS485 | smartrack/sensor/air_flow_1 | 10 | MATCH | airlow | Use all library variables; validate MQTT payload
SENSOR AIR QUALITY SR 1 C | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | smartrack/sensor/air_quality_1 | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
SENSOR TEMP HUM SR 1 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | smartrack/sensor/temp_hum_1 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM SR 2 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | smartrack/sensor/temp_hum_2 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
SENSOR TEMP HUM SR 3 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | smartrack/sensor/temp_hum_3 | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
BATTERY C 1 | Pilot | PBAT600 | Pilot-PBAT600 | battery | container/battery/battery_monitoring_system_1 | 10 | MATCH | string_serial_number, voltage_of_string_sensor, Charge_discharge_current_of_battery_string, string_soc, string_balancing_degree, string_status, string_cell_quantity, string_alarm, string_voltage_sum_of_cells, modbus_address, modbus_baudrate, specifications_of_hall_sensor, function_configuration, battery_capacity, types_of_battery_voltage, reference_value_of_battery_internal_resistance, the_quantity_of_cells_for_the_1st_COM, the_quantity_of_cells_for_the_2nd_COM, address_searching_status, cell_1_voltage, cell_2_voltage, cell_3_voltage, cell_4_voltage, cell_5_voltage, cell_6_voltage, cell_7_voltage, cell_8_voltage, cell_9_voltage, cell_10_voltage, cell_11_voltage, cell_12_voltage, cell_13_voltage, cell_14_voltage, cell_15_voltage, cell_16_voltage, cell_17_voltage, cell_18_voltage, cell_19_voltage, cell_20_voltage, cell_21_voltage, cell_22_voltage, cell_23_voltage, cell_24_voltage, cell_25_voltage, cell_26_voltage, cell_27_voltage, cell_28_voltage, cell_29_voltage, cell_30_voltage, cell_31_voltage, cell_32_voltage, cell_33_voltage, cell_34_voltage, cell_35_voltage, cell_36_voltage, cell_1_ohmic, cell_2_ohmic, cell_3_ohmic, cell_4_ohmic, cell_5_ohmic, cell_6_ohmic, cell_7_ohmic, cell_8_ohmic, cell_9_ohmic, cell_10_ohmic, cell_11_ohmic, cell_12_ohmic, cell_13_ohmic, cell_14_ohmic, cell_15_ohmic, cell_16_ohmic, cell_17_ohmic, cell_18_ohmic, cell_19_ohmic, cell_20_ohmic, cell_21_ohmic, cell_22_ohmic, cell_23_ohmic, cell_24_ohmic, cell_25_ohmic, cell_26_ohmic, cell_27_ohmic, cell_28_ohmic, cell_29_ohmic, cell_30_ohmic, cell_31_ohmic, cell_32_ohmic, cell_33_ohmic, cell_34_ohmic, cell_35_ohmic, cell_36_ohmic, cell_1_temperature, cell_2_temperature, cell_3_temperature, cell_4_temperature, cell_5_temperature, cell_6_temperature, cell_7_temperature, cell_8_temperature, cell_9_temperature, cell_10_temperature, cell_11_temperature, cell_12_temperature, cell_13_temperature, cell_14_temperature, cell_15_temperature, cell_16_temperature, cell_17_temperature, cell_18_temperature, cell_19_temperature, cell_20_temperature, cell_21_temperature, cell_22_temperature, cell_23_temperature, cell_24_temperature, cell_25_temperature, cell_26_temperature, cell_27_temperature, cell_28_temperature, cell_29_temperature, cell_30_temperature, cell_31_temperature, cell_32_temperature, cell_33_temperature, cell_34_temperature, cell_35_temperature, cell_36_temperature, cell_1_soc, cell_2_soc, cell_3_soc, cell_4_soc, cell_5_soc, cell_6_soc, cell_7_soc, cell_8_soc, cell_9_soc, cell_10_soc, cell_11_soc, cell_12_soc, cell_13_soc, cell_14_soc, cell_15_soc, cell_16_soc, cell_17_soc, cell_18_soc, cell_19_soc, cell_20_soc, cell_21_soc, cell_22_soc, cell_23_soc, cell_24_soc, cell_25_soc, cell_26_soc, cell_27_soc, cell_28_soc, cell_29_soc, cell_30_soc, cell_31_soc, cell_32_soc, cell_33_soc, cell_34_soc, cell_35_soc, cell_36_soc, cell_1_soh, cell_2_soh, cell_3_soh, cell_4_soh, cell_5_soh, cell_6_soh, cell_7_soh, cell_8_soh, cell_9_soh, cell_10_soh, cell_11_soh, cell_12_soh, cell_13_soh, cell_14_soh, cell_15_soh, cell_16_soh, cell_17_soh, cell_18_soh, cell_19_soh, cell_20_soh, cell_21_soh, cell_22_soh, cell_23_soh, cell_24_soh, cell_25_soh, cell_26_soh, cell_27_soh, cell_28_soh, cell_29_soh, cell_30_soh, cell_31_soh, cell_32_soh, cell_33_soh, cell_34_soh, cell_35_soh, cell_36_soh, cell_1_alarm, cell_2_alarm, cell_3_alarm, cell_4_alarm, cell_5_alarm, cell_6_alarm, cell_7_alarm, cell_8_alarm, cell_9_alarm, cell_10_alarm, cell_11_alarm, cell_12_alarm, cell_13_alarm, cell_14_alarm, cell_15_alarm, cell_16_alarm, cell_17_alarm, cell_18_alarm, cell_19_alarm, cell_20_alarm, cell_21_alarm, cell_22_alarm, cell_23_alarm, cell_24_alarm, cell_25_alarm, cell_26_alarm, cell_27_alarm, cell_28_alarm, cell_29_alarm, cell_30_alarm, cell_31_alarm, cell_32_alarm, cell_33_alarm, cell_34_alarm, cell_35_alarm, cell_36_alarm, cell_1_serial_number, cell_2_serial_number, cell_3_serial_number, cell_4_serial_number, cell_5_serial_number, cell_6_serial_number, cell_7_serial_number, cell_8_serial_number, cell_9_serial_number, cell_10_serial_number, cell_11_serial_number, cell_12_serial_number, cell_13_serial_number, cell_14_serial_number, cell_15_serial_number, cell_16_serial_number, cell_17_serial_number, cell_18_serial_number, cell_19_serial_number, cell_20_serial_number, cell_21_serial_number, cell_22_serial_number, cell_23_serial_number, cell_24_serial_number, cell_25_serial_number, cell_26_serial_number, cell_27_serial_number, cell_28_serial_number, cell_29_serial_number, cell_30_serial_number, cell_31_serial_number, cell_32_serial_number, cell_33_serial_number, cell_34_serial_number, cell_35_serial_number, cell_36_serial_number | Use all library variables; validate MQTT payload
SENSOR SUPER AIR FLOW C 1 | IOT | AirFlow_Sensor | IOT-AirFlow_Sensor | Sensor_RS485 | iot/modbus/air_flow | 10 | MATCH | airlow | Use all library variables; validate MQTT payload
Air-Quality (PM 2.5) Sensor & Output Control | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | iot/modbus/air_quality | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
Air & Ambient Pressure Monitor | IOT | AirPressure_Sensor | IOT-AirPressure_Sensor | Sensor_RS485 | iot/modbus/ambient_preasure | 10 | MATCH | positif_pressure, negatif_pressure, temperature_in_line_pressure | Use all library variables; validate MQTT payload
Two Low Power Relay 2 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay2 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
Two Low Power Relay 3 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay3 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
Two Solid State Relay 1 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay1 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
High Voltage SSR 1 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay4 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
Ambient Temperature Humidity Sensor 1 C | IOT | Temperature_Sensor | IOT-Temperature_Sensor | Sensor_RS485 | iot/modbus/temperature | 10 | MATCH | temp, hum | Use all library variables; validate MQTT payload
Two Low Power Relay 3 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay5 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
Two Low Power Relay 4 C | IOT | Relay | IOT-Relay | Sensor_RS485 | iot/modbus/relay6 | 10 | MATCH | Relay | Use all library variables; validate MQTT payload
Vibration Monitoring Sensor with High SSR Control 1 C | IOT | Vibration_Sensor | IOT-Vibration_Sensor | Sensor_RS485 | iot/modbus/vibration_sensor | 10 | MATCH | x, y, z, activity | Use all library variables; validate MQTT payload
POWER METER 1 C | ABB | M4M30 | ABB-M4M30 | power_meter | cpgs/power_meter/power_meter_2 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
POWER METER 2 C | ABB | M4M30 | ABB-M4M30 | power_meter | cpgs/power_meter/power_meter_3 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
Digital Input Remote Monitoring 2 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | modular/2/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Relay Remote Control 2 C | IOT | RELAYMINI | IOT-RELAYMINI |  | modular/2/minirelay/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Digital Input Remote Monitoring 1 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | modular/1/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Battery Monitoring System 1 C | Pilot | PBAT600 | Pilot-PBAT600 | battery | container/battery/battery_monitoring_system_1 | 10 | MATCH | string_serial_number, voltage_of_string_sensor, Charge_discharge_current_of_battery_string, string_soc, string_balancing_degree, string_status, string_cell_quantity, string_alarm, string_voltage_sum_of_cells, modbus_address, modbus_baudrate, specifications_of_hall_sensor, function_configuration, battery_capacity, types_of_battery_voltage, reference_value_of_battery_internal_resistance, the_quantity_of_cells_for_the_1st_COM, the_quantity_of_cells_for_the_2nd_COM, address_searching_status, cell_1_voltage, cell_2_voltage, cell_3_voltage, cell_4_voltage, cell_5_voltage, cell_6_voltage, cell_7_voltage, cell_8_voltage, cell_9_voltage, cell_10_voltage, cell_11_voltage, cell_12_voltage, cell_13_voltage, cell_14_voltage, cell_15_voltage, cell_16_voltage, cell_17_voltage, cell_18_voltage, cell_19_voltage, cell_20_voltage, cell_21_voltage, cell_22_voltage, cell_23_voltage, cell_24_voltage, cell_25_voltage, cell_26_voltage, cell_27_voltage, cell_28_voltage, cell_29_voltage, cell_30_voltage, cell_31_voltage, cell_32_voltage, cell_33_voltage, cell_34_voltage, cell_35_voltage, cell_36_voltage, cell_1_ohmic, cell_2_ohmic, cell_3_ohmic, cell_4_ohmic, cell_5_ohmic, cell_6_ohmic, cell_7_ohmic, cell_8_ohmic, cell_9_ohmic, cell_10_ohmic, cell_11_ohmic, cell_12_ohmic, cell_13_ohmic, cell_14_ohmic, cell_15_ohmic, cell_16_ohmic, cell_17_ohmic, cell_18_ohmic, cell_19_ohmic, cell_20_ohmic, cell_21_ohmic, cell_22_ohmic, cell_23_ohmic, cell_24_ohmic, cell_25_ohmic, cell_26_ohmic, cell_27_ohmic, cell_28_ohmic, cell_29_ohmic, cell_30_ohmic, cell_31_ohmic, cell_32_ohmic, cell_33_ohmic, cell_34_ohmic, cell_35_ohmic, cell_36_ohmic, cell_1_temperature, cell_2_temperature, cell_3_temperature, cell_4_temperature, cell_5_temperature, cell_6_temperature, cell_7_temperature, cell_8_temperature, cell_9_temperature, cell_10_temperature, cell_11_temperature, cell_12_temperature, cell_13_temperature, cell_14_temperature, cell_15_temperature, cell_16_temperature, cell_17_temperature, cell_18_temperature, cell_19_temperature, cell_20_temperature, cell_21_temperature, cell_22_temperature, cell_23_temperature, cell_24_temperature, cell_25_temperature, cell_26_temperature, cell_27_temperature, cell_28_temperature, cell_29_temperature, cell_30_temperature, cell_31_temperature, cell_32_temperature, cell_33_temperature, cell_34_temperature, cell_35_temperature, cell_36_temperature, cell_1_soc, cell_2_soc, cell_3_soc, cell_4_soc, cell_5_soc, cell_6_soc, cell_7_soc, cell_8_soc, cell_9_soc, cell_10_soc, cell_11_soc, cell_12_soc, cell_13_soc, cell_14_soc, cell_15_soc, cell_16_soc, cell_17_soc, cell_18_soc, cell_19_soc, cell_20_soc, cell_21_soc, cell_22_soc, cell_23_soc, cell_24_soc, cell_25_soc, cell_26_soc, cell_27_soc, cell_28_soc, cell_29_soc, cell_30_soc, cell_31_soc, cell_32_soc, cell_33_soc, cell_34_soc, cell_35_soc, cell_36_soc, cell_1_soh, cell_2_soh, cell_3_soh, cell_4_soh, cell_5_soh, cell_6_soh, cell_7_soh, cell_8_soh, cell_9_soh, cell_10_soh, cell_11_soh, cell_12_soh, cell_13_soh, cell_14_soh, cell_15_soh, cell_16_soh, cell_17_soh, cell_18_soh, cell_19_soh, cell_20_soh, cell_21_soh, cell_22_soh, cell_23_soh, cell_24_soh, cell_25_soh, cell_26_soh, cell_27_soh, cell_28_soh, cell_29_soh, cell_30_soh, cell_31_soh, cell_32_soh, cell_33_soh, cell_34_soh, cell_35_soh, cell_36_soh, cell_1_alarm, cell_2_alarm, cell_3_alarm, cell_4_alarm, cell_5_alarm, cell_6_alarm, cell_7_alarm, cell_8_alarm, cell_9_alarm, cell_10_alarm, cell_11_alarm, cell_12_alarm, cell_13_alarm, cell_14_alarm, cell_15_alarm, cell_16_alarm, cell_17_alarm, cell_18_alarm, cell_19_alarm, cell_20_alarm, cell_21_alarm, cell_22_alarm, cell_23_alarm, cell_24_alarm, cell_25_alarm, cell_26_alarm, cell_27_alarm, cell_28_alarm, cell_29_alarm, cell_30_alarm, cell_31_alarm, cell_32_alarm, cell_33_alarm, cell_34_alarm, cell_35_alarm, cell_36_alarm, cell_1_serial_number, cell_2_serial_number, cell_3_serial_number, cell_4_serial_number, cell_5_serial_number, cell_6_serial_number, cell_7_serial_number, cell_8_serial_number, cell_9_serial_number, cell_10_serial_number, cell_11_serial_number, cell_12_serial_number, cell_13_serial_number, cell_14_serial_number, cell_15_serial_number, cell_16_serial_number, cell_17_serial_number, cell_18_serial_number, cell_19_serial_number, cell_20_serial_number, cell_21_serial_number, cell_22_serial_number, cell_23_serial_number, cell_24_serial_number, cell_25_serial_number, cell_26_serial_number, cell_27_serial_number, cell_28_serial_number, cell_29_serial_number, cell_30_serial_number, cell_31_serial_number, cell_32_serial_number, cell_33_serial_number, cell_34_serial_number, cell_35_serial_number, cell_36_serial_number | Use all library variables; validate MQTT payload
Relay Remote Control 1 C | IOT | RELAYMINI | IOT-RELAYMINI |  | modular/1/minirelay/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Switch D-Link DGS 1210 10 C | D-Link | DGS-1210-10P | D-Link-DGS-1210-10P | switch | container/switch/dgs1210/1 | 10 | MATCH | sysSwitchName, sysHardwareVersion, sysFirmwareVersion, sysLocationName, sysIpAddr, sysIpSubnetMask, sysGateway, sysPortCtrlOperStatus_Port1, sysPortCtrlOperStatus_Port2, sysPortCtrlOperStatus_Port3, sysPortCtrlOperStatus_Port4, sysPortCtrlOperStatus_Port5, sysPortCtrlOperStatus_Port6, sysPortCtrlOperStatus_Port7, sysPortCtrlOperStatus_Port8, sysPortCtrlOperStatus_Port9, sysPortCtrlOperStatus_Port10, sysPortCtrlSpeed_Port1, sysPortCtrlSpeed_Port2, sysPortCtrlSpeed_Port3, sysPortCtrlSpeed_Port4, sysPortCtrlSpeed_Port5, sysPortCtrlSpeed_Port6, sysPortCtrlSpeed_Port7, sysPortCtrlSpeed_Port8, sysPortCtrlSpeed_Port9, sysPortCtrlSpeed_Port10, ifInOctets_Port1, ifInOctets_Port2, ifInOctets_Port3, ifInOctets_Port4, ifInOctets_Port5, ifInOctets_Port6, ifInOctets_Port7, ifInOctets_Port8, ifInOctets_Port9, ifInOctets_Port10, ifOutOctets_Port1, ifOutOctets_Port2, ifOutOctets_Port3, ifOutOctets_Port4, ifOutOctets_Port5, ifOutOctets_Port6, ifOutOctets_Port7, ifOutOctets_Port8, ifOutOctets_Port9, ifOutOctets_Port10, ifInErrors_Port1, ifInErrors_Port2, ifInErrors_Port3, ifInErrors_Port4, ifInErrors_Port5, ifInErrors_Port6, ifInErrors_Port7, ifInErrors_Port8, ifInErrors_Port9, ifInErrors_Port10, ifOutErrors_Port1, ifOutErrors_Port2, ifOutErrors_Port3, ifOutErrors_Port4, ifOutErrors_Port5, ifOutErrors_Port6, ifOutErrors_Port7, ifOutErrors_Port8, ifOutErrors_Port9, ifOutErrors_Port10, sysUpTime | Use all library variables; validate MQTT payload
POWER METER 1 C | ABB | M4M30 | ABB-M4M30 | power_meter | mobile_genset/power_meter/power_meter_1 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
Digital Input Remote Monitoring 3 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | mobilegenset/1/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Relay Remote Control 3 C | IOT | RELAYMINI | IOT-RELAYMINI |  | mobilegenset/1/minirelay/1 | 10 | GAP | - | Create/repair exact Device Library entry first
PWER METER LV 1 C | ABB | M4M30 | ABB-M4M30 | power_meter | kiosk_lvmdp/power_meter/power_meter_1 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
POWER METER MV 1 C | ABB | M4M30 | ABB-M4M30 | power_meter | kiosk_lvmdp/power_meter/power_meter_2 | 10 | MATCH | Three phase system voltage, Phase voltage L1, Phase voltage L2, Phase voltage L3, Line voltage L1-L2, Line voltage L3-L2, Line voltage L1-L3, Three phase system current, Current L1, Current L2, Current L3, Current N, Active power total, Active power L1, Active power L2, Active power L3, Reactive power total, Reactive power L1, Reactive power L2, Reactive power L3, Apparent power total, Apparent power L1, Apparent power L2, Apparent power L3, Frequency, Phase angles power total, Phase angles power L1, Phase angles power L2, Phase angles power L3, Phase angles voltage L1, Phase angles voltage L2, Phase angles voltage L3, Phase angles current L1, Phase angles current L2, Phase angles current L3, Power factor total, Power factor L1, Power factor L2, Power factor L3, Current quadrant total, Current quadrant L1, Current quadrant L2, Current quadrant L3, COSPHI TOT, COSPHI L1, COSPHI L2, COSPHI L3, Average current L1, Average current L2, Average current L3, Average current neutral, Average voltage L1, Average voltage L2, Average voltage L3, Average voltage L1-L2, Average voltage L2-L3, Average voltage L3-L1, Average active power total, Average active power L1, Average active power L2, Average active power L3, Average reactive power total, Average reactive power L1-L2, Average reactive power L2-L3, Average reactive power L3-L1, Average apparent power total, Average apparent power L1, Average apparent power L2, Average apparent power L3, Maximum current L1, Maximum current L2, Maximum current L3, Maximum current neutral, Maximum voltage L1, Maximum voltage L2, Maximum voltage L3, Maximum voltage L1-L2, Maximum voltage L2-Ll3, Maximum voltage L3-L1, Maximum Active power total, Maximum Active power L1, Maximum Active power L2, Maximum Active power L3, Maximum Reactive power total, Maximum Reactive power L1, Maximum Reactive power L2, Maximum Reactive power L3, Maximum Apparent power total, Maximum Apparent power L1, Maximum Apparent power L2, Maximum Apparent power L3, Minimum current L1, Minimum current L2, Minimum current L3, Minimum current neutral, Minimum voltage L1, Minimum voltage L2, Minimum voltage L3, Minimum voltage L1-L2, Minimum voltage L2-L3, Minimum voltage L3-L1, Minimum Active power total, Minimum Active power L1, Minimum Active power L2, Minimum Active power L3, Minimum Reactive power total, Minimum Reactive power L1, Minimum Reactive power L2, Minimum Reactive power L3, Minimum Apparent power total, Minimum Apparent power L1, Minimum Apparent power L2, Minimum Apparent power L3, Active energy - import, Active energy - export, Active energy - net, Reactive energy - import, Reactive energy - export, Reactive energy - net, Apparent energy - import, Apparent energy - export, Apparent energy - net, Active energy - import kg/kwh, Active energy - import Currency/kwh, Active energy - import tarfiffs, Active energy - export tarfiffs, Reactive energy - import tarfiffs, Reactive energy - export tarfiffs, Active energy - import L1, Active energy - import L2, Active energy - import L3, Active energy - export L1, Active energy - export L2, Active energy - export L3, Active energy - net L1, Active energy - net L2, Active energy - net L3, Reactive energy - import L1, Reactive energy - import L2, Reactive energy - import L3, Reactive energy - export L1, Reactive energy - export L2, Reactive energy - export L3, Reactive energy - net L1, Reactive energy - net L2, Reactive energy - net L3, Apparent energy - import L1, Apparent energy - import L2, Apparent energy - import L3, Apparent energy - export L1, Apparent energy - export L2, Apparent energy - export L3, Apparent energy - net L1, Apparent energy - net L2, Apparent energy - net L3, Voltage THD harmonics L1, Voltage THD harmonics L2, Voltage THD harmonics L3, Voltage THD harmonics L1-L2, Voltage THD harmonics L2-L3, Voltage THD harmonics L3-L1, Current harmonics THD L1, Current harmonics THD L2, Current harmonics THD L3, Current harmonics THD neutral, Unbalances phase voltage, Unbalances line voltage, Unbalances curremt | Use all library variables; validate MQTT payload
Digital Input Remote Monitoring 4 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | mv/1/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Digital Input Remote Monitoring 5 C | IOT | DRYCONTACT | IOT-DRYCONTACT | rectifier | smartrack/1/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Digital Input Remote Monitoring 6 C | IOT | DRYCONTACT | IOT-DRYCONTACT | rectifier | smartrack/2/drycontact/2 | 10 | GAP | - | Create/repair exact Device Library entry first
Relay Remote Control 4 C | IOT | RELAYMINI | IOT-RELAYMINI |  | smartrack/1/minirelay/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Digital Input Remote Monitoring 7 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | cpgs/1/drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
RECTIFIER ADDRAX 1 C | Addrax | TPML_SA50 | Addrax-TPML_SA50 | rectifier | lv/rectifier/addrax/1 | 10 | MATCH | System_Location, System_Manufacture, System_Serial_Number, System_Type, System_Name, Sytem_Site_Addres, is-Three-Phase-System, slave-Type, hardware-Version, serial-Number, ethernet-MAC-Address, AC_Voltage, phase-1-voltage, phase-2-voltage, phase-3-voltage, Load_Current, System_Power, Load_Power, number-Of-Registered-Rectifiers, number-Of-Registered-Failed, number-Of-Registered-Comms-Lost, Rectifier_Current, Rectifier_Current_Limit, enable-Current-Share, highest-Rectifier-Heatsink-Temperature, Values-Index-rectifier, Serial-Number-rectifier, Status-rectifier, Maximum-Current-Limit-rectifier, Maximum-Power-Limit-rectifier, Minimum-OVSD-Set-Point-rectifier, Maximum-OVSD-Set-Point-rectifier, Reported-AC-Voltage-rectifier, Reported-Voltage-rectifier, Reported-Current-rectifier, Output-Power-rectifier, Heatsink-Temperature-rectifier, Registration-State-rectifier, Failed-State-rectifier, load-Based-Run-Time-rectifier, shutdown-Rectifier, Has-Been-Shutdown-rectifier, Phase-1-rectifier, Phase-2-rectifier, Phase-3-rectifier, rectifier-Shutdown-Mode, restart-All-Rectifiers, rect-Cycle-Low-Threshold, rect-Cycle-High-Threshold, rect-Cycle-Interval, reset-Run-Times, ramp-Up-Slope, ovsd-Set-Point, rectifier-Start-Up-Delay, control-State, maximum-System-Voltage, float-Voltage, minimum-System-Voltage, bus-Voltage, target-Voltage, avc-State, avc-Offset, base-Voltage, temperature-Compensation-Allowed, temperature-Compensation-State, temperature-Compensation-Slope, temperature-Compensation-Reference-Temperature, temperature-Compensation-Upper-Limit, temperature-Compensation-Lower-Limit, temperature-Compensation-Offset-Voltage, reset-Battery-State, enable-Equalize, equalize-Start-Allowed, equalize-State, equalize-Voltage, equalize-Offset-Voltage, equalize-Interval, next-Equalize-Start-Time, equalize-Duration, equalize-Remaining-Time, start-Equalize, stop-Equalize, enable-Fast-Charge, fast-Charge-State, fast-Charge-Start-Allowed, fast-Charge-Voltage, fast-Charge-Offset-Voltage, fast-Charge-Ah-Discharged, fast-Charge-Maximum-Duration, fast-Charge-Ampere-Hour-Threshold, fast-Charge-Voltage-Threshold, fast-Charge-Recharge-Percentage, fast-Charge-Ampere-Hour-Stop-Threshold, fast-Charge-Maximum-Time-Remaining, stop-Fast-Charge, enable-Battery-Current-Limit, enable-Battery-Current-Limit, bcl-State, generator-State, bcl-Limit, bcl-Offset-Voltage, bcl-Engine-Run-Limit, enable-Battery-Test, battery-Test-Start-Allowed, battery-Test-Lockout-Remaining, battery-Test-State, battery-Test-First-Date-Time, battery-Test-Interval, next-Battery-Test-Start-Time, battery-Test-Duration, battery-Test-Remaining-Time, battery-Test-Termination-Voltage, battery-Test-Offset-Voltage, start-Battery-Test, stop-Battery-Test, lvd-Inhibit-Period, allow-Front-Panel-LVD-Control, lvd-Index, lvd-State, lvd-Inhibited, enable-LVD-Voltage-Disconnect, lvd-Disconnect-Voltage, lvd-Reconnect-Voltage, lvd-Recognition-Period, enable-LVD-AC-Timer, lvd-AC-Timer-Disconnect-Delay, enable-LVD-Chained-To-Previous, lvdc-Index, lvdc-LVD-Mapping, lvdc-State, enable-LVDC, lvdc-IOB-Number, lvdc-IOB-LVD-Number, lvdc-Type, generator-Fail-Alarm-Recognition-Period, generator-On-Fast-Charge, generator-On-Equalize, generator-On-Mains-Failure, ac-Supply-State, generator-Run-Time-Remaining, generator-Refuel-Volume, generator-Backup-Time, fuel-Level, generator-Control-Relay, generator-Startup-Wiring, manual-Generator-Run-Time, fuel-Tank-Volume, manual-Generator-Start, manual-Generator-Stop, clear-Fuel-Consumption-History, controller-Time, analog-Input-Index, ai-High-State, ai-Low-State, ai-Value, ai-Status, ai-Name, ai-Units, ai-IOB-Number, input-Number, gain, offset, hysteresis, high-Severity, high-Threshold, high-DO-Mapping-A, high-DO-Mapping-B, high-Send-Trap, low-Severity, low-Threshold, low-DO-Mapping-A, low-DO-Mapping-B, low-Send-Trap, ai-High-Notes, ai-Low-Notes, alternative-Source-Current, mains-Fail, fan-Fail, mov-Fail, load-Fuse-Fail, battery-Fuse-Fail, phase-Fail, battery-Capacity, digital-Input-Index, di-State, di-Value, di-Status, di-Name, di-IOB-Number, digital-Input-Number, di-Severity, di-Recognition-Period, di-Deactivation-Recognition-Period, di-DO-Mapping-A, di-DO-Mapping-B, di-Send-Trap, di-Active-State, di-Notes, digital-Output-Index, do-State, remote-Control-State, do-Status, do-Name, do-IOB-Number, do-IOB-DO-Number, do-Active-State, battery-Capacity, cells-Per-String, battery-Temperature, battery-Current, battery-Type, battery-Charge-State, battery-State-Threshold, end-Of-Charge-Action, mpm-Lockout-Period, mpm-Convergence-Period, string-Fail-Recognition-Period, mpm-Start-Threshold, midpoint-Monitoring-String-Index, string-Name, string-State, midpoint-Voltage, imbalance-Percent, mpm-State, time-In-This-Statee, current-MPM-Threshold, reference-Voltage, clear-String-Fail, summary-Alarm-Critical, summary-Alarm-Major, summary-Alarm-Minor, reset-Rectifier-Comms-Lost-Alarm, reset-Battery-Test-Failed-Alarm, alarm-Index, alarm-Name, alarm-Severity, alarm-State, alarm-Notes, enable-Audible-Alarm-Indication, alarm-Recognition-Period, ac-Fail-Recognition-Period, enable-High-Float-Tracking, high-Float-Threshold, enable-Low-Float-Tracking, low-Float-Threshold, high-Load-Threshold, low-Load-Threshold, battery-Temperature-High-Threshold, battery-Temperature-Low-Threshold, system-Overload-Type, system-Overload-Recognition-Period, system-Overload-Threshold, in-Discharge-Alarm-Condition, battery-Current-Sensor-Fail-Recognition-Period | Use all library variables; validate MQTT payload
Digital Input Remote Monitoring 7 C | IOT | RELAYMINI | IOT-RELAYMINI |  | IOT/Acrylic/RelayMini/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Relay Remote Control 5 C | IOT | DRYCONTACT | IOT-DRYCONTACT |  | IOT/Acrylic/Drycontact/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Air Quality Sensor 1 C | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | limbah/airquality1/sps30 | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
Air Quality Sensor 2 C | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | limbah/airquality2/sps30 | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
Air Quality Sensor 1 C (SHT4x) | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | limbah/airquality1/sht4x | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
Air Quality Sensor 2 C (SHT4x) | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | limbah/airquality2/sht4x | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
Sensor PH 1 C | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph1 | 10 | GAP | - | Create/repair exact Device Library entry first
Sensor PH 2 C | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph2 | 10 | GAP | - | Create/repair exact Device Library entry first
Sensor PH 3 C | SeedStudio | S_pH_01 | SeedStudio-S_pH_01 | water | limbah/ph3 | 10 | GAP | - | Create/repair exact Device Library entry first
Water Flow Sensor 1 C | Taosonic | TUF2000M | Taosonic-TUF2000M | water | limbah/flow1 | 10 | GAP | - | Create/repair exact Device Library entry first
Water Flow Sensor 2 C | Taosonic | TUF2000M | Taosonic-TUF2000M | water | limbah/flow2 | 10 | GAP | - | Create/repair exact Device Library entry first
Vibration Sensor 1 C | IOT | ENVAIRQUALITYV1 | IOT-ENVAIRQUALITYV1 | environment | limbah/airquality1/lis3dhtr | 10 | MATCH | CO, NH3, NO2, LPGValue, DetectLPG | Use all library variables; validate MQTT payload
YFB6_Waterflow 1 | Taosonic | TUF2000M | Taosonic-TUF2000M | water | gspesensor/wtrflw/1 | 10 | GAP | - | Create/repair exact Device Library entry first
YFB6_Waterflow 2 | Taosonic | TUF2000M | Taosonic-TUF2000M | water | gspesensor/wtrflw/2 | 10 | GAP | - | Create/repair exact Device Library entry first
YFB6_Waterflow 3 | Taosonic | TUF2000M | Taosonic-TUF2000M | water | gspesensor/wtrflw/3 | 10 | GAP | - | Create/repair exact Device Library entry first
YFB6_Waterflow 4 | Taosonic | TUF2000M | Taosonic-TUF2000M | water | gspesensor/wtrflw/4 | 10 | GAP | - | Create/repair exact Device Library entry first
Power Meter Mesin Laser | Pilot | SPM33 | Pilot-SPM33 | power_meter | spm33/2 | 10 | MATCH | Neutral_current, Current_phase_A, Current_phase_B, Current_phase_C, Line_AB_voltage, Line_BC_voltage, Line_CA_voltage, Voltage_phase_A, Voltage_phase_B, Voltage_phase_C, Total_power, Total_reactive_power, Total_apparent_power, Power_faktor_average, Frequency, Total_harmonic_distortion_voltage_phase_A, Total_harmonic_distortion_voltage_phase_B, Total_harmonic_distortion_voltage_phase_C, Total_harmonic_distortion_current_phase_A, Total_harmonic_distortion_current_phase_B, Total_harmonic_distortion_current_phase_C, Total_energy_aktif, Total_energy_reactive, Total_3rd_harmonic_distortion_voltage_phase_A, Total_3rd_harmonic_distortion_voltage_phase_B, Total_3rd_harmonic_distortion_voltage_phase_C, Total_5rd_harmonic_distortion_voltage_phase_A, Total_5rd_harmonic_distortion_voltage_phase_B, Total_5rd_harmonic_distortion_voltage_phase_C, Total_3rd_harmonic_distortion_current_phase_A, Total_3rd_harmonic_distortion_current_phase_B, Total_3rd_harmonic_distortion_current_phase_C, Total_5rd_harmonic_distortion_current_phase_A, Total_5rd_harmonic_distortion_current_phase_B, Total_5rd_harmonic_distortion_current_phase_C, Total_power_Factor | Use all library variables; validate MQTT payload
Power Meter Mesin Punching dan Bending | Pilot | SPM33 | Pilot-SPM33 | power_meter | spm33/3 | 10 | MATCH | Neutral_current, Current_phase_A, Current_phase_B, Current_phase_C, Line_AB_voltage, Line_BC_voltage, Line_CA_voltage, Voltage_phase_A, Voltage_phase_B, Voltage_phase_C, Total_power, Total_reactive_power, Total_apparent_power, Power_faktor_average, Frequency, Total_harmonic_distortion_voltage_phase_A, Total_harmonic_distortion_voltage_phase_B, Total_harmonic_distortion_voltage_phase_C, Total_harmonic_distortion_current_phase_A, Total_harmonic_distortion_current_phase_B, Total_harmonic_distortion_current_phase_C, Total_energy_aktif, Total_energy_reactive, Total_3rd_harmonic_distortion_voltage_phase_A, Total_3rd_harmonic_distortion_voltage_phase_B, Total_3rd_harmonic_distortion_voltage_phase_C, Total_5rd_harmonic_distortion_voltage_phase_A, Total_5rd_harmonic_distortion_voltage_phase_B, Total_5rd_harmonic_distortion_voltage_phase_C, Total_3rd_harmonic_distortion_current_phase_A, Total_3rd_harmonic_distortion_current_phase_B, Total_3rd_harmonic_distortion_current_phase_C, Total_5rd_harmonic_distortion_current_phase_A, Total_5rd_harmonic_distortion_current_phase_B, Total_5rd_harmonic_distortion_current_phase_C, Total_power_Factor | Use all library variables; validate MQTT payload
ATS 4 | ABB | ATS022 | ATS-Controller | switch | container/ats/ats_1 | 10 | MATCH | Status, Alarms, CB1 Status, CB2 Status, CB3 Status, Generator Alarm, Logic Locked, Force Commutation, Generator Start, Switching Enabled, Remote Reset, Emergency Lock, LN1_V1_voltage, LN1_V2_voltage, LN1_V3_voltage, LN1_V12_voltage, LN1_V23_voltage, LN1_V31_voltage, LN2_V1_voltage, LN2_V2_voltage, LN2_V3_voltage, LN2_V12_voltage, LN2_V23_voltage, LN2_V31_voltage, LN1_freq, LN2_freq, Alarm/Event 1 (newest), Alarm/Event 2, Alarm/Event 3, Alarm/Event 4, Alarm/Event 5, Device Status, Protection Devices, Nominal Voltage | Use all library variables; validate MQTT payload
UPS 5 | Hitachi | HR11 | Hitachi-HR11 | ups | container/ups/ups_1 | 10 | MATCH | ups_model, ups_firmware_version, battery_full_charge_voltage, input_voltage, frequency, output_status, output_voltage, load_percentage, battery_status, battery_voltage, battery_temperature | Use all library variables; validate MQTT payload
Genset Controller 11 | Deepsea_Electronic | DSE8610MKII | DeepSea-DSE8610MKII | Controller | mobile_genset/genset_ctrl/genset_ctrl_1 | 10 | MATCH | Oil pressure, Coolant temperature, Oil temperature, Fuel level, Charge alternator voltage, Engine Battery voltage, Engine speed, Generator frequency, Generator L1-N voltage, Generator L2-N voltage, Generator L3-N voltage, Generator L1-L2 voltage, Generator L2-L3 voltage, Generator L3-L1 voltage, Generator L1 current, Generator L2 current, Generator L3 current, Generator earth current, Generator L1 watts , Generator L2 watts , Generator L3 watts , Generator current lag/lead, Mains frequency, Mains L1-N voltage, Mains L2-N voltage, Mains L3-N voltage, Mains L1-L2 voltage, Mains L2-L3 voltage, Mains L3-L1 voltage, Mains voltage phase lag/lead, Generator phase rotation, Mains phase rotation, Mains current lag/lead, Mains L1 current, Mains L2 current, Mains L3 current, Mains earth current, Mains L1 watts, Mains L2 watts, Mains L3 watts, Bus current lag/lead, Bus frequency, Bus L1-N voltage, Bus L2-N voltage, Bus L3-N voltage, Bus L1-L2 voltage, Bus L2-L3 voltage, Bus L3-L1 voltage, Bus L1 current, Bus L2 current, Bus L3 current, Bus earth current, Bus L1 watts, Bus L2 watts, Bus L3 watts, Bus phase rotation, Gorvernor Output, AVR Output, Coolant pressure 1, Coolant pressure 2, Fuel pressure 1, Fuel pressure 2, Turbo pressure 1, Turbo pressure 2, Inlet manifold temperature 1, Inlet manifold temperature 2, xhaust temperature 1, xhaust temperature 2, Fuel consumption, Water in Fuel, CAN BIT data, Atmospheric pressure, Fuel temperature, Fuel level (Units) <8xxx phase 2>, Selected units for fuel level <8xxx phase 2>, Auxiliary sender 1 category, Auxiliary sender 1 value, Auxiliary sender 2 category, Auxiliary sender 2 value, Auxiliary sender 3 category, Auxiliary sender 3 value, Auxiliary sender 4 category, Auxiliary sender 4 value, Exhaust after treatment fuel used, After treatment temperature T1, After treatment temperature T3, Engine reference torque, Engine percentage torque, Engine demand torque, Percentage load at speed, Accelerator position, Nominal friction percentage torque, Oil level, Crank case pressure, Coolant level, Injector Rail 1 pressure, Injector Rail 2 pressure, Engine EGR flow, Pre filter oil pressure, Instant break power, Exhaust gas port 1 temperature, Exhaust gas port 2 temperature, Exhaust gas port 3 temperature, Exhaust gas port 4 temperature, Exhaust gas port 5 temperature, Exhaust gas port 6 temperature, Exhaust gas port 7 temperature, Exhaust gas port 8 temperature, Exhaust gas port 9 temperature, Exhaust gas port 10 temperature, Exhaust gas port 11 temperature, Exhaust gas port 12 temperature, Exhaust gas port 13 temperature, Exhaust gas port 14 temperature, Exhaust gas port 15 temperature, Exhaust gas port 16 temperature, Intercooler temperature, Turbo oil temperature, ECU temperature, Fan speed, Total engine revolutions, Air inlet pressure, Air filter differential pressure, Air trap inlet pressure, Turbo pressure 3, Turbo pressure 4, Inlet manifold temperature 3, Inlet manifold temperature 4, Inlet manifold temperature 5, Inlet manifold temperature 6, Trip fuel, Electrical potential, PGI Engine type, PGI Engine version number, DPTC filter lamp command, Exhaust system high temperature lamp, DPTC Action regeneration forced, Shutdown wait to start, Shutdown protection, Shutdown Approaching, Engine operating state, Shutdown coolant override, Battle short override, Module engine hours, Module oil pressure, Module coolant temperature, Module engine RPM, Module charge alternator, Module speed feed, Frequency adjust, Engine operating state 1, Engine alarm warning, Engine alarm shutdown, Engine alarm electrical trip, CAN amber stop lamp, CAN amber lamp flash, CAN Red stop lamp, CAN red lamp flash, CAN protect lamp, CAN protect lamp flash, Malfunction Lamp, Malfunction lamp flash, Electrical potential, Battery potential, Charging potential, Charge alternator current, Battery current, Engine torque mode, Engine starter mode, CAN CI status, Demand speed, Speed up, Speed down, Speed fail, Current SD source, Feedback SD CAN, Feedback SD analogue, Failure codes, Actual droop, Start status, Protection override status, MTU running state, Cylinder cut off, Load gen status, Extended stop status, Current operating mode, MTU required torque, Trip average fuel, ECU rated power, ECU rated speed, ECU idle speed, ECU desired speed, ECU preheat status, Manifold pressure, Intercooler level, CAN link status, Auto DPF Regeneration Inhibit, DPTC Active Regeneration Inhibit Switch (received from engine) SPN 3703, Battery Charger Current Limit, Battery Charger PCB Temperature, Battery Charger Calculated Ambient Temperature, LCD Temperature, Manufacturer code, Control mode, Battery Charger Mode, Battery Charger De-Rating Mode, Battery ChargerActive Cell Count, Charging States, Generator total watts, Generator L1 VA, Generator L2 VA, Generator L3 VA, Generator total VA, Generator L1 VAr, Generator L2 VAr, Generator L3 VAr, Generator total VAr, Generator power factor L1, Generator power factor L2, Generator power factor L3, Generator average power factor, Generator percentage of full power, Generator percentage of full VAr, Mains total watts, Mains L1 VA, Mains L2 VA, Mains L3 VA, Mains total VA, Mains L1 VAr, Mains L2 VAr, Mains L3 VAr, Mains total VA, Mains power factor L1, Mains power factor L2, Mains power factor L3, Mains average power factor, Mains percentage of full power, Mains percentage of full VAr, Bus total watts, Bus L1 Va, Bus L2 Va, Bus L3 Va, Bus total VA, Bus L1 Var, Bus L2 Var, Bus L3 Var, Bus total VAr, Bus power faktor L1, Bus power faktor L2, Bus power faktor L3, Bus average power factor, Bus percentage of full powerr, Bus percentage of full Var, Load total watts, Load total var, Mains R.O.C.O.F., Mains vector shift, Gen L1 lead /lag, Gen L2 lead /lag, Gen L3 lead /lag, Gen total lead /lag, Gen L1 percentage of full power, Gen L2 percentage of full power, Gen L3 percentage of full power, Bus 2 average power factor, Bus 2 total watts, Bus 2 L1 VA, Bus 2 L2 VA, Bus 2 L3 VA, Bus 2 total VA, Bus 2 L1 VAr, Bus 2 L2 VAr, Bus 2 L3 VAr, Bus 2 total VAr, Bus 2 power factor L1, Bus 2 power factor L2, Bus 2 power factor L3, Bus 2 percentage of full power, Bus 2 percentage of full VAr, Mains L1 lead/lag, Mains L2 lead/lag, Mains L3 lead/lag, Mains total lead/lag, Generator L-N voltage average, Generator L-N voltage difference, Generator L-N voltage min, Generator L-N voltage max, Generator L-L voltage average, Generator L-L voltage difference, Generator L-L voltage min, Generator L-L voltage max, Generator current average, Generator current difference, Generator current min, Generator current max, Generator watts average, Generator watts difference, Generator watts min, Generator watts max, Generator VA average, Generator VA difference, Generator VA min, Generator VA max, Generator VAr average, Generator VAr difference, Generator VAr min, Generator VAr max, Generator power factor average, Generator power factor difference, Generator power factor min, Generator power factor max, Mains L-N voltage average, Mains L-N voltage difference, Mains L-N voltage min, Mains L-N voltage max, Mains L-L voltage average, Mains L-L voltage difference, Mains L-L voltage min, Mains L-L voltage max, Bus L-N voltage average, Bus L-N voltage difference, Bus L-N voltage min, Bus L-N voltage max, Bus L-L voltage average, Bus L-L voltage difference, Bus L-L voltage min, Bus L-L voltage max, Bus 2 L-N voltage average, Bus 2 L-N voltage difference, Bus 2 L-N voltage min, Bus 2 L-N voltage max, Bus 2 L-L voltage average, Bus 2 L-L voltage difference, Bus 2 L-L voltage min, Bus 2 L-L voltage max, DC Charger Watts, DC Load Watts, DC Battery Watts, DC Total Watts, DC percentage of full power, Time To Empty (87xx v5.3), Number of named alarms, Alarm1, Alarm2, Alarm3, Alarm4, Alarm5, Alarm6, Alarm7, Alarm8, Alarm9, Alarm10, Alarm11, Alarm12, Alarm13, Alarm14, Alarm15, Alarm16, Alarm17, Alarm18, Alarm19, Alarm20, Alarm21, Alarm22, Alarm23, Alarm24, Alarm25, Alarm26, Alarm27, Alarm28, Alarm29, Alarm30, Alarm31, Alarm32, Alarm33, Alarm34, Alarm35, Alarm36, Alarm37, Alarm38, Alarm39, Digital Input 1, Digital Input 2, Number of unnamed digital inputs, Unnamed digital input 1-16, Unnamed digital input 17-32, Unnamed digital input 33-48, Unnamed digital input 49-64, Unnamed digital input 65-80, Unnamed digital input 81-96, Unnamed digital input 97-112, Unnamed digital input 113-128 | Use all library variables; validate MQTT payload
UPS (Smartrack) | Hitachi | HR11 | Smartrack-UPS | ups | smartrack/ups/ups_1 | 10 | MATCH | ups_model, ups_firmware_version, battery_full_charge_voltage, input_voltage, frequency, output_status, output_voltage, load_percentage, battery_status, battery_voltage, battery_temperature | Use all library variables; validate MQTT payload
Rectifier (SC503) | DPC | SC501 | DPC-SC501 | rectifier | smartrack/rectifier/sc503/1 | 10 | MATCH | AC_Online_Status, Battery_State, Battery_voltage_current, Ambient Temperature, AC_Input_1_Voltage_Phase_A, AC_Input_1_Voltage_Phase_B, AC_Input_1_Voltage_Phase_C, AC_Input_2_Voltage_Phase_A, AC_Input_2_Voltage_Phase_B, AC_Input_2_Voltage_Phase_C, AC_Input_1_Current_Phase_A, AC_Input_1_Current_Phase_B, AC_Input_1_Current_Phase_C, AC_Input_2_Current_Phase_A, AC_Input_2_Current_Phase_B, AC_Input_2_Current_Phase_C, AC_Input_1_Active_Power_Phase_A, AC_Input_1_Active_Power_Phase_B, AC_Input_1_Active_Power_Phase_C, AC_Input_2_Active_Power_Phase_A, AC_Input_2_Active_Power_Phase_B, AC_Input_2_Active_Power_Phase_C, AC_Input_1_Reactive_Power_Phase_A, AC_Input_1_Reactive_Power_Phase_B, AC_Input_1_Reactive_Power_Phase_C, AC_Input_2_Reactive_Power_Phase_A, AC_Input_2_Reactive_Power_Phase_B, AC_Input_2_Reactive_Power_Phase_C, AC_Input_1_Apparent_Power_Phase_A, AC_Input_1_Apparent_Power_Phase_B, AC_Input_1_Apparent_Power_Phase_C, AC_Input_2_Apparent_Power_Phase_A, AC_Input_2_Apparent_Power_Phase_B, AC_Input_2_Apparent_Power_Phase_C, AC_Input_1_Active_Energy_Phase_A, AC_Input_1_Active_Energy_Phase_B, AC_Input_1_Active_Energy_Phase_C, AC_Input_2_Active_Energy_Phase_A, AC_Input_2_Active_Energy_Phase_B, AC_Input_2_Active_Energy_Phase_C, AC_Input_1_Reactive_Energy_Phase_A, AC_Input_1_Reactive_Energy_Phase_B, AC_Input_1_Reactive_Energy_Phase_C, AC_Input_2_Reactive_Energy_Phase_A, AC_Input_2_Reactive_Energy_Phase_B, AC_Input_2_Reactive_Energy_Phase_C, AC_Input_1_Apparent_Energy_Phase_A, AC_Input_1_Apparent_Energy_Phase_B, AC_Input_1_Apparent_Energy_Phase_C, AC_Input_2_Apparent_Energy_Phase_A, AC_Input_2_Apparent_Energy_Phase_B, AC_Input_2_Apparent_Energy_Phase_C, AC_Input_1_Frequency_Phase_A, AC_Input_1_Frequency_Phase_B, AC_Input_1_Frequency_Phase_C, AC_Input_2_Frequency_Energy_Phase_A, AC_Input_2_Frequency_Phase_B, AC_Input_2_Frequency_Phase_C, AC_Input_1_Last_Month_Energy, AC_Input_1_Curent_Month_Energy, AC_Input_2_Last_Month_Energy, AC_Input_2_Curent_Month_Energy, Number_of_Installed_Rectifiers, Number_of_Fault_Rectifier, Load_Rate, Output_Current_of_Rectifiers, Type_Rectifier, Vin, Vout, Output_Current, Ambient_Temperature, Primary_Hot_Temperature, Secondary_Hot_Temperature, Out_Current_Limit, Number_of_branches, Bus_Voltage, DC_Energy, Load_Current, Battery_Status, Battery_1_Capacity, Battery_2_Capacity, Battery_3_Capacity, Battery_4_Capacity, Battery_5_Capacity, Battery_6_Capacity, Battery_7_Capacity, Battery_8_Capacity, Voltage(BMS), Current(BMS), Cycle_Counts(BMS), Total_Capacity(BMS), SOC(BMS), SOH(BMS), Ambient_Temperature(BMS), Maximum_Voltage(BMS), Minimum_Voltage(BMS), Average_Voltage(BMS), Temperature_Batt_1, Temperature_Batt_2, EX-Temperature_1, EX-Temperature_2, Amb_Temperature, Humidity, AC_Alarm_1, DC_Alarm_1, DC_Total_Load_Slight_Over_Current, DC_Total_Load_Severe_Over_Current, System_SPD_Fault, System_Total_Alarm, BMS1_communication_fault, Temperature_sensor_1_not_assemble, Temperature_sensor_2_not_assemble, EX-Temperature_sensor_1_not_assemble, EX-Temperature_sensor_2_not_assemble, LLVD_Alarm, BLVD_Alarm, LLVD1_Fail, LLVD2_Fail, LLVD3_Fail, LLVD4_Fail, LLVD5_Fail, LLVD6_Fail, LLVD7_Fail, LLVD8_Fail, BLVD_Fail, PreAlarm-LLVD1, PreAlarm-LLVD2, PreAlarm-LLVD3, PreAlarm-LLVD4, PreAlarm-LLVD5, PreAlarm-LLVD6, PreAlarm-LLVD7, PreAlarm-LLVD8, PreAlarm-BLVD, Battery_Break, Ambient_High1_Temperature, Ambient_High2_Temperature, Battery_Charge_Over_current, Battery_Discharge, Battery_Cycle_Test_Over_current, Battery_Middle_Imbalance, Battery_Can_Not_Charge, DC_Branch_Slight_Over_Current, DC_Branch_Severe_Over_Current, Load_Break, Load_Break_, Ambient_Temperature_Low1, Ambient_Temperature_Low2, Humidity_High, Humidity_Low, Battery_Temperature_High1, Battery_Temperature_High2, Battery_Temperature_Low1, Battery_Temperature_Low2, BTRM_High_1, BTRM_High_2, AC_System_Alarm, DC_System_Alarm | Use all library variables; validate MQTT payload
Inverter (SC350) | DPC | SC503 | DPC-SC503 | rectifier | smartrack/rectifier/sc350/1 | 10 | GAP | - | Create/repair exact Device Library entry first
Lux Sensor Control Monitoring 19 | IOT | LuxSensor | IOT-LuxSensor | sensor | iot/modbus/lux_sensor | 10 | GAP | - | Create/repair exact Device Library entry first
Temp Hum Sensor 1 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/1 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 2 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/2 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 3 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/3 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 4 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/4 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 5 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/5 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 6 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/6 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 7 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/7 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 8 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/8 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 9 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/9 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 10 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/10 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 11 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/11 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 12 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/12 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Temp Hum Sensor 13 | Sensirion | SHT40 | Sensirion-SHT40 | environment | rack/container/temp_humidity/13 | 10 | MATCH | Temperature, Humidity | Use all library variables; validate MQTT payload
Air Flow Sensor 1 | Renesas | FS3000-1005 | Renesas-FS3000-1005 | environment | rack/container/airflow/1 | 10 | MATCH | AirVelocity | Use all library variables; validate MQTT payload
Air Pressure Sensor 1 | Sensirion | SDP810-125 | Sensirion-SDP810-125 | environment | rack/container/air_pressure/1 | 10 | MATCH | Pressure, Temperature | Use all library variables; validate MQTT payload
Dry Contact Sensor 1 | IOT | Dry_Contact | IOT-Dry_Contact | Sensor_RS485 | rack/container/dry_contact/1 | 10 | MATCH | dry_contact | Use all library variables; validate MQTT payload
Rack PDU 1 | APC | AP8881 | APC-AP8881 | pdu | rack/container/pdu/1 | 10 | MATCH | Device_Model, Device_Name, Device_Location, Device_Serial_Number, Device_Long_Description, Device_NMC_Serial_Number, Number_of_Outlets, Number_of_Switched_Outlets, Number_of_Metered_Outlets, Number_of_Phases, Number_of_Banks, Max_Current_Rating, Outlet_Layout, Max_Phase_Current_Rating, Device_Power_Rating, Device_Load_State, Device_Power, Device_Energy, Device_Power_Supply_Alarm, Device_Power_Supply_1_Status, Device_Power_Supply_2_Status, Device_Apparent_Power, Device_Power_Factor, Phase_Table_Size, Phase_Load_State, Phase_Current, Phase_Voltage, Phase_Power, Phase_Apparent_Power, Phase_Power_Factor, Phase_Peak_Current, Bank_Table_Size, Bank_Load_State, Bank_Current, Bank_Peak_Current, Outlet_Switched_Table_Size, Outlet_Switched_State, Outlet_Switched_Command_Pending, Outlet_Metered_Table_Size, Outlet_Metered_State, Outlet_Metered_Current, Outlet_Metered_Power, Outlet_Metered_Energy, Sensor_Temp_Humidity_Table_Size, Sensor_Comm_Status, Sensor_Temperature_C, Sensor_Relative_Humidity, Sensor_Humidity_Status | Use all library variables; validate MQTT payload
Rack PDU 2 | APC | AP8881 | APC-AP8881 | pdu | rack/container/pdu/2 | 10 | MATCH | Device_Model, Device_Name, Device_Location, Device_Serial_Number, Device_Long_Description, Device_NMC_Serial_Number, Number_of_Outlets, Number_of_Switched_Outlets, Number_of_Metered_Outlets, Number_of_Phases, Number_of_Banks, Max_Current_Rating, Outlet_Layout, Max_Phase_Current_Rating, Device_Power_Rating, Device_Load_State, Device_Power, Device_Energy, Device_Power_Supply_Alarm, Device_Power_Supply_1_Status, Device_Power_Supply_2_Status, Device_Apparent_Power, Device_Power_Factor, Phase_Table_Size, Phase_Load_State, Phase_Current, Phase_Voltage, Phase_Power, Phase_Apparent_Power, Phase_Power_Factor, Phase_Peak_Current, Bank_Table_Size, Bank_Load_State, Bank_Current, Bank_Peak_Current, Outlet_Switched_Table_Size, Outlet_Switched_State, Outlet_Switched_Command_Pending, Outlet_Metered_Table_Size, Outlet_Metered_State, Outlet_Metered_Current, Outlet_Metered_Power, Outlet_Metered_Energy, Sensor_Temp_Humidity_Table_Size, Sensor_Comm_Status, Sensor_Temperature_C, Sensor_Relative_Humidity, Sensor_Humidity_Status | Use all library variables; validate MQTT payload
Rack PDU 3 | APC | AP8881 | APC-AP8881 | pdu | rack/container/pdu/3 | 10 | MATCH | Device_Model, Device_Name, Device_Location, Device_Serial_Number, Device_Long_Description, Device_NMC_Serial_Number, Number_of_Outlets, Number_of_Switched_Outlets, Number_of_Metered_Outlets, Number_of_Phases, Number_of_Banks, Max_Current_Rating, Outlet_Layout, Max_Phase_Current_Rating, Device_Power_Rating, Device_Load_State, Device_Power, Device_Energy, Device_Power_Supply_Alarm, Device_Power_Supply_1_Status, Device_Power_Supply_2_Status, Device_Apparent_Power, Device_Power_Factor, Phase_Table_Size, Phase_Load_State, Phase_Current, Phase_Voltage, Phase_Power, Phase_Apparent_Power, Phase_Power_Factor, Phase_Peak_Current, Bank_Table_Size, Bank_Load_State, Bank_Current, Bank_Peak_Current, Outlet_Switched_Table_Size, Outlet_Switched_State, Outlet_Switched_Command_Pending, Outlet_Metered_Table_Size, Outlet_Metered_State, Outlet_Metered_Current, Outlet_Metered_Power, Outlet_Metered_Energy, Sensor_Temp_Humidity_Table_Size, Sensor_Comm_Status, Sensor_Temperature_C, Sensor_Relative_Humidity, Sensor_Humidity_Status | Use all library variables; validate MQTT payload
Rack PDU 4 | APC | AP8881 | APC-AP8881 | pdu | rack/container/pdu/4 | 10 | MATCH | Device_Model, Device_Name, Device_Location, Device_Serial_Number, Device_Long_Description, Device_NMC_Serial_Number, Number_of_Outlets, Number_of_Switched_Outlets, Number_of_Metered_Outlets, Number_of_Phases, Number_of_Banks, Max_Current_Rating, Outlet_Layout, Max_Phase_Current_Rating, Device_Power_Rating, Device_Load_State, Device_Power, Device_Energy, Device_Power_Supply_Alarm, Device_Power_Supply_1_Status, Device_Power_Supply_2_Status, Device_Apparent_Power, Device_Power_Factor, Phase_Table_Size, Phase_Load_State, Phase_Current, Phase_Voltage, Phase_Power, Phase_Apparent_Power, Phase_Power_Factor, Phase_Peak_Current, Bank_Table_Size, Bank_Load_State, Bank_Current, Bank_Peak_Current, Outlet_Switched_Table_Size, Outlet_Switched_State, Outlet_Switched_Command_Pending, Outlet_Metered_Table_Size, Outlet_Metered_State, Outlet_Metered_Current, Outlet_Metered_Power, Outlet_Metered_Energy, Sensor_Temp_Humidity_Table_Size, Sensor_Comm_Status, Sensor_Temperature_C, Sensor_Relative_Humidity, Sensor_Humidity_Status | Use all library variables; validate MQTT payload
Rack PDU 5 | APC | AP8881 | APC-AP8881 | pdu | rack/container/pdu/5 | 10 | MATCH | Device_Model, Device_Name, Device_Location, Device_Serial_Number, Device_Long_Description, Device_NMC_Serial_Number, Number_of_Outlets, Number_of_Switched_Outlets, Number_of_Metered_Outlets, Number_of_Phases, Number_of_Banks, Max_Current_Rating, Outlet_Layout, Max_Phase_Current_Rating, Device_Power_Rating, Device_Load_State, Device_Power, Device_Energy, Device_Power_Supply_Alarm, Device_Power_Supply_1_Status, Device_Power_Supply_2_Status, Device_Apparent_Power, Device_Power_Factor, Phase_Table_Size, Phase_Load_State, Phase_Current, Phase_Voltage, Phase_Power, Phase_Apparent_Power, Phase_Power_Factor, Phase_Peak_Current, Bank_Table_Size, Bank_Load_State, Bank_Current, Bank_Peak_Current, Outlet_Switched_Table_Size, Outlet_Switched_State, Outlet_Switched_Command_Pending, Outlet_Metered_Table_Size, Outlet_Metered_State, Outlet_Metered_Current, Outlet_Metered_Power, Outlet_Metered_Energy, Sensor_Temp_Humidity_Table_Size, Sensor_Comm_Status, Sensor_Temperature_C, Sensor_Relative_Humidity, Sensor_Humidity_Status | Use all library variables; validate MQTT payload
Cooling Unit 1 | Schneider | ACRD301P | Schneider-ACRD301P | aircond | rack/container/cooling/1 | 10 | MATCH | Group_Minimum_Rack_Temperature_C, Group_Maximum_Rack_Temperature_C, Total_Airflow_LS, Total_Airflow_CFM, Total_Air_Side_Cooling_Demand_kW, Supply_Average_Temperature_C, Supply_Average_Temperature_F, Return_Average_Temperature_C, Return_Average_Temperature_F, Humidity_RH, Airflow_LS, Airflow_CFM, Air_Filter_Pressure_Pa, Air_Filter_Pressure_InWC, Supply_Air_Setpoint_C, Supply_Air_Setpoint_F, Cool_Setpoint_C, Cool_Setpoint_F, Unit, Startup_Delay, Cooling_Strategy, Maximum_Fan_Speed, Manual_IT_Fan_Speed, Unit_Role_Override, Idle_On_Leak_Detect, Shutdown_Input_State, Shutdown_Input_Present, Shutdown_Input_Normal_State, Protect_On_Standby, Power_Feed_Type, Active_Flow_Control_Status, Mode, Shutdown_Input_State_Status, Alarm_Relay_1, Alarm_Relay_2, Alarm_Relay_3, Alarm_Relay_4 | Use all library variables; validate MQTT payload
Cooling Unit 2 | Schneider | ACRD301P | Schneider-ACRD301P | aircond | rack/container/cooling/2 | 10 | MATCH | Group_Minimum_Rack_Temperature_C, Group_Maximum_Rack_Temperature_C, Total_Airflow_LS, Total_Airflow_CFM, Total_Air_Side_Cooling_Demand_kW, Supply_Average_Temperature_C, Supply_Average_Temperature_F, Return_Average_Temperature_C, Return_Average_Temperature_F, Humidity_RH, Airflow_LS, Airflow_CFM, Air_Filter_Pressure_Pa, Air_Filter_Pressure_InWC, Supply_Air_Setpoint_C, Supply_Air_Setpoint_F, Cool_Setpoint_C, Cool_Setpoint_F, Unit, Startup_Delay, Cooling_Strategy, Maximum_Fan_Speed, Manual_IT_Fan_Speed, Unit_Role_Override, Idle_On_Leak_Detect, Shutdown_Input_State, Shutdown_Input_Present, Shutdown_Input_Normal_State, Protect_On_Standby, Power_Feed_Type, Active_Flow_Control_Status, Mode, Shutdown_Input_State_Status, Alarm_Relay_1, Alarm_Relay_2, Alarm_Relay_3, Alarm_Relay_4 | Use all library variables; validate MQTT payload
Power Meter LV Panel 1 | Schneider | PM5650 | Schneider-PM5650 | power_meter | rack/container/power_meter/1 | 10 | MATCH | Nominal_Frequency, Nominal_Voltage, Nominal_Current, Normal_Phase_Rotation, Logical_Phase_A_Voltage, Logical_Phase_B_Voltage, Logical_Phase_C_Voltage, Logical_Phase_N_Voltage, Logical_Phase_A_Current, Logical_Phase_B_Current, Logical_Phase_C_Current, Logical_Phase_N_Current, Peak_Current_Demand_Over_Last_Year, Active_Load_Timer_Setpoint, Active_Energy_Delivered_Into_Load, Active_Energy_Received_Out_of_Load, Active_Energy_Delivered_Received, Active_Energy_Delivered_Received_Diff, Reactive_Energy_Delivered, Reactive_Energy_Received, Reactive_Energy_Delivered_Received, Reactive_Energy_Delivered_Received_Diff, Apparent_Energy_Delivered, Apparent_Energy_Received, Apparent_Energy_Delivered_Received, Apparent_Energy_Delivered_Received_Diff, Current_Phase_A, Current_Phase_B, Current_Phase_C, Current_Phase_N, Current_Phase_G, Current_3_Phase_Average, Current_Unbalance_Phase_A, Current_Unbalance_Phase_B, Current_Unbalance_Phase_C, Current_Unbalance_Phase_Worst, Voltage_A_B, Voltage_B_C, Voltage_C_A, Voltage_L_L_Avg, Voltage_A_N, Voltage_B_N, Voltage_C_N, Voltage_L_N_Avg, Voltage_Unbalance_A_B, Voltage_Unbalance_B_C, Voltage_Unbalance_C_A, Voltage_Unbalance_Max_L_L, Voltage_Unbalance_A_N, Voltage_Unbalance_B_N, Voltage_Unbalance_C_N, Voltage_Unbalance_Max_L_N, Active_Power_Phase_A, Active_Power_Phase_B, Active_Power_Phase_C, Active_Power_Total, Reactive_Power_Phase_A, Reactive_Power_Phase_B, Reactive_Power_Phase_C, Reactive_Power_Total, Apparent_Power_Phase_A, Apparent_Power_Phase_B, Apparent_Power_Phase_C, Apparent_Power_Total, Frequency, Temperature | Use all library variables; validate MQTT payload
Power Meter LV Panel 2 | Schneider | PM5650 | Schneider-PM5650 | power_meter | rack/container/power_meter/2 | 10 | MATCH | Nominal_Frequency, Nominal_Voltage, Nominal_Current, Normal_Phase_Rotation, Logical_Phase_A_Voltage, Logical_Phase_B_Voltage, Logical_Phase_C_Voltage, Logical_Phase_N_Voltage, Logical_Phase_A_Current, Logical_Phase_B_Current, Logical_Phase_C_Current, Logical_Phase_N_Current, Peak_Current_Demand_Over_Last_Year, Active_Load_Timer_Setpoint, Active_Energy_Delivered_Into_Load, Active_Energy_Received_Out_of_Load, Active_Energy_Delivered_Received, Active_Energy_Delivered_Received_Diff, Reactive_Energy_Delivered, Reactive_Energy_Received, Reactive_Energy_Delivered_Received, Reactive_Energy_Delivered_Received_Diff, Apparent_Energy_Delivered, Apparent_Energy_Received, Apparent_Energy_Delivered_Received, Apparent_Energy_Delivered_Received_Diff, Current_Phase_A, Current_Phase_B, Current_Phase_C, Current_Phase_N, Current_Phase_G, Current_3_Phase_Average, Current_Unbalance_Phase_A, Current_Unbalance_Phase_B, Current_Unbalance_Phase_C, Current_Unbalance_Phase_Worst, Voltage_A_B, Voltage_B_C, Voltage_C_A, Voltage_L_L_Avg, Voltage_A_N, Voltage_B_N, Voltage_C_N, Voltage_L_N_Avg, Voltage_Unbalance_A_B, Voltage_Unbalance_B_C, Voltage_Unbalance_C_A, Voltage_Unbalance_Max_L_L, Voltage_Unbalance_A_N, Voltage_Unbalance_B_N, Voltage_Unbalance_C_N, Voltage_Unbalance_Max_L_N, Active_Power_Phase_A, Active_Power_Phase_B, Active_Power_Phase_C, Active_Power_Total, Reactive_Power_Phase_A, Reactive_Power_Phase_B, Reactive_Power_Phase_C, Reactive_Power_Total, Apparent_Power_Phase_A, Apparent_Power_Phase_B, Apparent_Power_Phase_C, Apparent_Power_Total, Frequency, Temperature | Use all library variables; validate MQTT payload
ATS LV Panel | Schneider | TA63D4L4004TPE | Schneider-TA63D4L4004TPE | switch | rack/container/ats/1 | 10 | MATCH | Switch_Position, Normal_Source_State, Alternate_Source_State, Common_Register_1006_Status, Common_Register_1007_Status, Common_Register_1008_Status, SII_Voltage_Unbalance_Rate, SII_VCN, Source_Rated_Voltage, Source_Rated_Frequency, Source_Neutral_Position, Enable_Abnormal_Frequency_Transfer, SI_Under_Frequency_Dropout_Threshold_Percent, SI_Under_Frequency_Pickup_Threshold_Percent, SII_Under_Frequency_Dropout_Threshold_Percent, SII_Under_Frequency_Pickup_Threshold_Percent, SII_Under_Voltage_Dropout_Threshold_Value, SII_Under_Voltage_Pickup_Threshold_Value, SI_Over_Voltage_Dropout_Threshold_Value, SI_Over_Voltage_Pickup_Threshold_Value, SII_Over_Voltage_Dropout_Threshold_Value, SII_Over_Voltage_Pickup_Threshold_Value, Genset_Start_Failure_Alarm, External_Power_Supply_Presence, Onload_Test_Failure_Alarm, Offload_Test_Failure_Alarm, Unexpected_Position_Alarm, Total_Transfer_Count, Total_Transfer_Failure_Count, Too_Fast_Transfer_Counter, Configuration_Changed_Count | Use all library variables; validate MQTT payload
UPS Battery Panel | Schneider | EMUPS50K250QBHS | Schneider-EMUPS50K250QBHS | ups | rack/container/ups/1 | 10 | MATCH | ups_model, ups_name, ups_firmware_revision, ups_manufacture_date, ups_serial_number, ups_sku_number, ups_apparent_power_rating, battery_status, battery_time_on_battery, battery_last_replace_date, battery_capacity, battery_temperature_advanced, battery_runtime_remaining, battery_replace_indicator, battery_num_of_packs, battery_num_of_bad_packs, battery_full_capacity, battery_temperature, battery_actual_voltage, battery_current, battery_health, input_phase, input_voltage, input_frequency, input_line_fail_cause, input_nominal_voltage, input_total_apparent_power, input_total_active_power, input_energy_usage, phase_input_voltage_L1, phase_input_voltage_L2, phase_input_voltage_L3, phase_input_current_L1, phase_input_current_L2, phase_input_current_L3, phase_input_power_L1, phase_input_power_L2, phase_input_power_L3, output_status, system_status, internal_ups_temperature, output_voltage, output_frequency, output_load, output_current, output_efficiency, output_energy_usage, output_active_power, output_apparent_power, output_redundancy, phase_output_voltage_L1, phase_output_voltage_L2, phase_output_voltage_L3, phase_output_current_L1, phase_output_current_L2, phase_output_current_L3, phase_output_load_L1, phase_output_load_L2, phase_output_load_L3, phase_output_power_L1, phase_output_power_L2, phase_output_power_L3, phase_output_percent_load_L1, phase_output_percent_load_L2, phase_output_percent_load_L3, phase_output_power_factor_L1, phase_output_power_factor_L2, phase_output_power_factor_L3, state_output_flags, state_alarm_status, state_abnormal_conditions, state_3phase_specific_faults, state_system_messages, state_total_time_on_battery, state_ecomode, state_lifecycle_management, test_diagnostics_results, test_last_diagnostics_date, test_battery_process_status, test_battery_condition_status | Use all library variables; validate MQTT payload

## Device Library Variables
Category | Manufacturer | Part Number | Protocol | Default Address | Variable | Register/OID | Register Type | Word Length | Data Type | Multiplier | Write Access | Library Rule
aircond | Schneider | ACRD301P | SNMP |  | Group_Minimum_Rack_Temperature_C | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Group_Maximum_Rack_Temperature_C | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.3 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Total_Airflow_LS | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.5 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Total_Airflow_CFM | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.6 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Total_Air_Side_Cooling_Demand_kW | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.7 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Supply_Average_Temperature_C | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.9 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Supply_Average_Temperature_F | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.10 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Return_Average_Temperature_C | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.13 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Return_Average_Temperature_F | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.14 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Humidity_RH | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.15 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Airflow_LS | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.16 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Airflow_CFM | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.17 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Air_Filter_Pressure_Pa | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.18 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Air_Filter_Pressure_InWC | .1.3.6.1.4.1.318.1.1.27.1.4.1.2.1.3.19 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Supply_Air_Setpoint_C | .1.3.6.1.4.1.318.1.1.27.1.5.1.2.1.3.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Supply_Air_Setpoint_F | .1.3.6.1.4.1.318.1.1.27.1.5.1.2.1.3.2 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Cool_Setpoint_C | .1.3.6.1.4.1.318.1.1.27.1.5.1.2.1.3.3 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Cool_Setpoint_F | .1.3.6.1.4.1.318.1.1.27.1.5.1.2.1.3.4 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Unit | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Startup_Delay | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Cooling_Strategy | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Maximum_Fan_Speed | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.4 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Manual_IT_Fan_Speed | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.5 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Unit_Role_Override | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.6 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Idle_On_Leak_Detect | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.7 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Shutdown_Input_State | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.8 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Shutdown_Input_Present | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.9 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Shutdown_Input_Normal_State | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.10 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Protect_On_Standby | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.11 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Power_Feed_Type | .1.3.6.1.4.1.318.1.1.27.1.5.2.2.1.4.12 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Active_Flow_Control_Status | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Mode | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Shutdown_Input_State_Status | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Alarm_Relay_1 | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.4 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Alarm_Relay_2 | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.5 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Alarm_Relay_3 | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.6 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
aircond | Schneider | ACRD301P | SNMP |  | Alarm_Relay_4 | .1.3.6.1.4.1.318.1.1.27.1.4.2.2.1.4.7 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Device_Manufacture | 1.3.6.1.4.1.850.1.1.1.2.1.4.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Device_Model | 1.3.6.1.4.1.850.1.1.1.2.1.5.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Phases_Voltage | .1.3.6.1.4.1.850.1.1.3.2.3.1.2.1.4.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Number_of_Phases | .1.3.6.1.4.1.850.1.1.3.2.3.1.2.1.1.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Output_Voltage | .1.3.6.1.4.1.850.1.1.3.2.3.1.1.1.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Output_Current_Bank_1 | .1.3.6.1.4.1.850.1.1.3.2.3.4.1.1.4.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Output_Current_Bank_2 | .1.3.6.1.4.1.850.1.1.3.2.3.4.1.1.4.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Number_of_Outlets | .1.3.6.1.4.1.850.1.1.3.2.1.2.1.4.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | InputFrequency | .1.3.6.1.4.1.850.1.1.3.2.3.1.2.1.3.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Low_Transfer_Voltage | .1.3.6.1.4.1.850.1.1.3.2.3.1.1.1.4.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Current_Limit_Maximum | .1.3.6.1.4.1.850.1.1.3.2.3.2.1.1.7.1.1 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Voltage_Minimum | .1.3.6.1.4.1.850.1.1.3.2.3.1.2.1.5.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Voltage Maximum | .1.3.6.1.4.1.850.1.1.3.2.3.1.2.1.6.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Bank_Breaker_1_Status | .1.3.6.1.4.1.850.1.1.3.2.3.5.1.1.2.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Bank_Breaker_2_Status | .1.3.6.1.4.1.850.1.1.3.2.3.5.1.1.2.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | Tripplite | PDUMNV32HV2LX | SNMP |  | Number_of_Alarm | .1.3.6.1.4.1.850.1.3.1.0 | SNMP OID |  | ALARMTYPE | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Model | .1.3.6.1.4.1.318.1.1.26.2.1.8.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Name | .1.3.6.1.4.1.318.1.1.26.2.1.3.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Location | .1.3.6.1.4.1.318.1.1.26.2.1.4.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Serial_Number | .1.3.6.1.4.1.318.1.1.26.2.1.9.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Long_Description | .1.3.6.1.4.1.318.1.1.26.2.1.12.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_NMC_Serial_Number | .1.3.6.1.4.1.318.1.1.26.2.1.13.1 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Number_of_Outlets | .1.3.6.1.4.1.318.1.1.26.4.2.1.4.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Number_of_Switched_Outlets | .1.3.6.1.4.1.318.1.1.26.4.2.1.5.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Number_of_Metered_Outlets | .1.3.6.1.4.1.318.1.1.26.4.2.1.6.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Number_of_Phases | .1.3.6.1.4.1.318.1.1.26.4.2.1.7.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Number_of_Banks | .1.3.6.1.4.1.318.1.1.26.4.2.1.8.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Max_Current_Rating | .1.3.6.1.4.1.318.1.1.26.4.2.1.9.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Layout | .1.3.6.1.4.1.318.1.1.26.4.2.1.11.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Max_Phase_Current_Rating | .1.3.6.1.4.1.318.1.1.26.4.2.1.12.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power_Rating | .1.3.6.1.4.1.318.1.1.26.4.2.1.13.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Load_State | .1.3.6.1.4.1.318.1.1.26.4.3.1.4.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power | .1.3.6.1.4.1.318.1.1.26.4.3.1.5.1 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Energy | .1.3.6.1.4.1.318.1.1.26.4.3.1.9.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power_Supply_Alarm | .1.3.6.1.4.1.318.1.1.26.4.3.1.12.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power_Supply_1_Status | .1.3.6.1.4.1.318.1.1.26.4.3.1.13.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power_Supply_2_Status | .1.3.6.1.4.1.318.1.1.26.4.3.1.14.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Apparent_Power | .1.3.6.1.4.1.318.1.1.26.4.3.1.16.1 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Device_Power_Factor | .1.3.6.1.4.1.318.1.1.26.4.3.1.17.1 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Table_Size | .1.3.6.1.4.1.318.1.1.26.5.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Load_State | .1.3.6.1.4.1.318.1.1.26.6.3.1.4.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Current | .1.3.6.1.4.1.318.1.1.26.6.3.1.5.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Voltage | .1.3.6.1.4.1.318.1.1.26.6.3.1.6.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Power | .1.3.6.1.4.1.318.1.1.26.6.3.1.7.x | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Apparent_Power | .1.3.6.1.4.1.318.1.1.26.6.3.1.8.x | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Power_Factor | .1.3.6.1.4.1.318.1.1.26.6.3.1.9.x | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Phase_Peak_Current | .1.3.6.1.4.1.318.1.1.26.6.3.1.10.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Bank_Table_Size | .1.3.6.1.4.1.318.1.1.26.7.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Bank_Load_State | .1.3.6.1.4.1.318.1.1.26.8.3.1.4.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Bank_Current | .1.3.6.1.4.1.318.1.1.26.8.3.1.5.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Bank_Peak_Current | .1.3.6.1.4.1.318.1.1.26.8.3.1.6.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Switched_Table_Size | .1.3.6.1.4.1.318.1.1.26.9.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Switched_State | .1.3.6.1.4.1.318.1.1.26.9.2.3.1.5.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Switched_Command_Pending | .1.3.6.1.4.1.318.1.1.26.9.2.3.1.6.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Metered_Table_Size | .1.3.6.1.4.1.318.1.1.26.9.3.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Metered_State | .1.3.6.1.4.1.318.1.1.26.9.4.3.1.5.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Metered_Current | .1.3.6.1.4.1.318.1.1.26.9.4.3.1.6.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Metered_Power | .1.3.6.1.4.1.318.1.1.26.9.4.3.1.7.x | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Outlet_Metered_Energy | .1.3.6.1.4.1.318.1.1.26.9.4.3.1.11.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Sensor_Temp_Humidity_Table_Size | .1.3.6.1.4.1.318.1.1.26.10.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Sensor_Comm_Status | .1.3.6.1.4.1.318.1.1.26.10.2.3.1.6.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Sensor_Temperature_C | .1.3.6.1.4.1.318.1.1.26.10.2.3.1.8.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Sensor_Relative_Humidity | .1.3.6.1.4.1.318.1.1.26.10.2.3.1.10.x | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
pdu | APC | AP8881 | SNMP |  | Sensor_Humidity_Status | .1.3.6.1.4.1.318.1.1.26.10.2.3.1.11.x | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_model | .1.3.6.1.4.1.318.1.1.1.1.1.1.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_name | .1.3.6.1.4.1.318.1.1.1.1.1.2.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_firmware_revision | .1.3.6.1.4.1.318.1.1.1.1.2.1.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_manufacture_date | .1.3.6.1.4.1.318.1.1.1.1.2.2.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_serial_number | .1.3.6.1.4.1.318.1.1.1.1.2.3.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_sku_number | .1.3.6.1.4.1.318.1.1.1.1.2.5.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | ups_apparent_power_rating | .1.3.6.1.4.1.318.1.1.1.1.2.9.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_status | .1.3.6.1.4.1.318.1.1.1.2.1.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_time_on_battery | .1.3.6.1.4.1.318.1.1.1.2.1.2.0 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_last_replace_date | .1.3.6.1.4.1.318.1.1.1.2.1.3.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_capacity | .1.3.6.1.4.1.318.1.1.1.2.2.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_temperature_advanced | .1.3.6.1.4.1.318.1.1.1.2.2.2.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_runtime_remaining | .1.3.6.1.4.1.318.1.1.1.2.2.3.0 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_replace_indicator | .1.3.6.1.4.1.318.1.1.1.2.2.4.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_num_of_packs | .1.3.6.1.4.1.318.1.1.1.2.2.5.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_num_of_bad_packs | .1.3.6.1.4.1.318.1.1.1.2.2.6.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_full_capacity | .1.3.6.1.4.1.318.1.1.1.2.2.11.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_temperature | .1.3.6.1.4.1.318.1.1.1.2.3.2.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_actual_voltage | .1.3.6.1.4.1.318.1.1.1.2.3.4.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_current | .1.3.6.1.4.1.318.1.1.1.2.3.5.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | battery_health | .1.3.6.1.4.1.318.1.1.1.2.3.11.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_phase | .1.3.6.1.4.1.318.1.1.1.3.1.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_voltage | .1.3.6.1.4.1.318.1.1.1.3.3.1.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_frequency | .1.3.6.1.4.1.318.1.1.1.3.3.4.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_line_fail_cause | .1.3.6.1.4.1.318.1.1.1.3.2.5.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_nominal_voltage | .1.3.6.1.4.1.318.1.1.1.3.2.7.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_total_apparent_power | .1.3.6.1.4.1.318.1.1.1.3.2.11.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_total_active_power | .1.3.6.1.4.1.318.1.1.1.3.2.12.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | input_energy_usage | .1.3.6.1.4.1.318.1.1.1.3.2.15.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_voltage_L1 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_voltage_L2 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_voltage_L3 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_current_L1 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_current_L2 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.2 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_current_L3 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.3 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_power_L1 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.9.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_power_L2 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.9.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_input_power_L3 | .1.3.6.1.4.1.318.1.1.1.9.2.3.1.9.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_status | .1.3.6.1.4.1.318.1.1.1.4.1.1.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | system_status | .1.3.6.1.4.1.318.1.1.1.4.1.3.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | internal_ups_temperature | .1.3.6.1.4.1.318.1.1.1.4.1.4.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_voltage | .1.3.6.1.4.1.318.1.1.1.4.3.1.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_frequency | .1.3.6.1.4.1.318.1.1.1.4.3.2.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_load | .1.3.6.1.4.1.318.1.1.1.4.3.3.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_current | .1.3.6.1.4.1.318.1.1.1.4.3.4.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_efficiency | .1.3.6.1.4.1.318.1.1.1.4.3.5.0 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_energy_usage | .1.3.6.1.4.1.318.1.1.1.4.3.6.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_active_power | .1.3.6.1.4.1.318.1.1.1.4.2.8.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_apparent_power | .1.3.6.1.4.1.318.1.1.1.4.2.9.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | output_redundancy | .1.3.6.1.4.1.318.1.1.1.4.2.5.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_voltage_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_voltage_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_voltage_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_current_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.1 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_current_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.2 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_current_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.3 | SNMP OID |  | INTEGER | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_load_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.7.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_load_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.7.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_load_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.7.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.13.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.13.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.13.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_percent_load_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.10.1.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_percent_load_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.10.1.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_percent_load_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.10.1.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_factor_L1 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.19.1.1 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_factor_L2 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.19.1.2 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | phase_output_power_factor_L3 | .1.3.6.1.4.1.318.1.1.1.9.3.3.1.19.1.3 | SNMP OID |  | INTEGER | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_output_flags | .1.3.6.1.4.1.318.1.1.1.11.1.1.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_alarm_status | .1.3.6.1.4.1.318.1.1.1.11.1.2.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_abnormal_conditions | .1.3.6.1.4.1.318.1.1.1.11.2.1.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_3phase_specific_faults | .1.3.6.1.4.1.318.1.1.1.11.2.2.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_system_messages | .1.3.6.1.4.1.318.1.1.1.11.2.6.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_total_time_on_battery | .1.3.6.1.4.1.318.1.1.1.11.2.7.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_ecomode | .1.3.6.1.4.1.318.1.1.1.11.2.13.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | state_lifecycle_management | .1.3.6.1.4.1.318.1.1.1.11.2.14.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | test_diagnostics_results | .1.3.6.1.4.1.318.1.1.1.7.2.3.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | test_last_diagnostics_date | .1.3.6.1.4.1.318.1.1.1.7.2.4.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | test_battery_process_status | .1.3.6.1.4.1.318.1.1.1.7.2.14.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
ups | Schneider | EMUPS50K250QBHS | SNMP |  | test_battery_condition_status | .1.3.6.1.4.1.318.1.1.1.7.2.15.0 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_serial_number | 11 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | voltage_of_string_sensor | 0 | Holding Register | 2 | UINT32 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | Charge_discharge_current_of_battery_string | 2 | Holding Register | 2 | UINT32 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_soc | 4 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_balancing_degree | 6 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_status | 7 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_cell_quantity | 10 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_alarm | 13 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | string_voltage_sum_of_cells | 20 | Holding Register | 2 | UINT32 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | modbus_address | 100 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | modbus_baudrate | 101 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | specifications_of_hall_sensor | 102 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | function_configuration | 103 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | battery_capacity | 107 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | types_of_battery_voltage | 108 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | reference_value_of_battery_internal_resistance | 109 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | the_quantity_of_cells_for_the_1st_COM | 120 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | the_quantity_of_cells_for_the_2nd_COM | 130 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | address_searching_status | 6001 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_voltage | 1600 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_voltage | 1601 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_voltage | 1602 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_voltage | 1603 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_voltage | 1604 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_voltage | 1605 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_voltage | 1606 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_voltage | 1607 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_voltage | 1608 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_voltage | 1609 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_voltage | 1610 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_voltage | 1611 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_voltage | 1612 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_voltage | 1613 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_voltage | 1614 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_voltage | 1615 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_voltage | 1616 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_voltage | 1617 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_voltage | 1618 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_voltage | 1619 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_voltage | 1620 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_voltage | 1621 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_voltage | 1622 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_voltage | 1623 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_voltage | 1624 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_voltage | 1625 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_voltage | 1626 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_voltage | 1627 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_voltage | 1628 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_voltage | 1629 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_voltage | 1630 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_voltage | 1631 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_voltage | 1632 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_voltage | 1633 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_voltage | 1634 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_voltage | 1635 | Holding Register | 1 | UINT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_ohmic | 1900 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_ohmic | 1901 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_ohmic | 1902 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_ohmic | 1903 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_ohmic | 1904 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_ohmic | 1905 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_ohmic | 1906 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_ohmic | 1907 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_ohmic | 1908 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_ohmic | 1909 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_ohmic | 1910 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_ohmic | 1911 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_ohmic | 1912 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_ohmic | 1913 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_ohmic | 1914 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_ohmic | 1915 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_ohmic | 1916 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_ohmic | 1917 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_ohmic | 1918 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_ohmic | 1919 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_ohmic | 1920 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_ohmic | 1921 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_ohmic | 1922 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_ohmic | 1923 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_ohmic | 1924 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_ohmic | 1925 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_ohmic | 1926 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_ohmic | 1927 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_ohmic | 1928 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_ohmic | 1929 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_ohmic | 1930 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_ohmic | 1931 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_ohmic | 1932 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_ohmic | 1933 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_ohmic | 1934 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_ohmic | 1935 | Holding Register | 2 | UINT32 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_temperature | 2500 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_temperature | 2501 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_temperature | 2502 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_temperature | 2503 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_temperature | 2504 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_temperature | 2505 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_temperature | 2506 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_temperature | 2507 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_temperature | 2508 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_temperature | 2509 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_temperature | 2510 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_temperature | 2511 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_temperature | 2512 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_temperature | 2513 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_temperature | 2514 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_temperature | 2515 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_temperature | 2516 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_temperature | 2517 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_temperature | 2518 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_temperature | 2519 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_temperature | 2520 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_temperature | 2521 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_temperature | 2522 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_temperature | 2523 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_temperature | 2524 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_temperature | 2525 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_temperature | 2526 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_temperature | 2527 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_temperature | 2528 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_temperature | 2529 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_temperature | 2530 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_temperature | 2531 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_temperature | 2532 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_temperature | 2533 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_temperature | 2534 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_temperature | 2535 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_soc | 2800 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_soc | 2801 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_soc | 2802 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_soc | 2803 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_soc | 2804 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_soc | 2805 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_soc | 2806 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_soc | 2807 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_soc | 2808 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_soc | 2809 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_soc | 2810 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_soc | 2811 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_soc | 2812 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_soc | 2813 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_soc | 2814 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_soc | 2815 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_soc | 2816 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_soc | 2817 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_soc | 2818 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_soc | 2819 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_soc | 2820 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_soc | 2821 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_soc | 2822 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_soc | 2823 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_soc | 2824 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_soc | 2825 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_soc | 2826 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_soc | 2827 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_soc | 2828 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_soc | 2829 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_soc | 2830 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_soc | 2831 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_soc | 2832 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_soc | 2833 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_soc | 2834 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_soc | 2835 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_soh | 3100 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_soh | 3101 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_soh | 3102 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_soh | 3103 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_soh | 3104 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_soh | 3105 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_soh | 3106 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_soh | 3107 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_soh | 3108 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_soh | 3109 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_soh | 3110 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_soh | 3111 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_soh | 3112 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_soh | 3113 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_soh | 3114 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_soh | 3115 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_soh | 3116 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_soh | 3117 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_soh | 3118 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_soh | 3119 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_soh | 3120 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_soh | 3121 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_soh | 3122 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_soh | 3123 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_soh | 3124 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_soh | 3125 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_soh | 3126 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_soh | 3127 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_soh | 3128 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_soh | 3129 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_soh | 3130 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_soh | 3131 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_soh | 3132 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_soh | 3133 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_soh | 3134 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_soh | 3135 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_alarm | 3400 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_alarm | 3401 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_alarm | 3402 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_alarm | 3403 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_alarm | 3404 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_alarm | 3405 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_alarm | 3406 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_alarm | 3407 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_alarm | 3408 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_alarm | 3409 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_alarm | 3410 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_alarm | 3411 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_alarm | 3412 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_alarm | 3413 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_alarm | 3414 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_alarm | 3415 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_alarm | 3416 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_alarm | 3417 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_alarm | 3418 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_alarm | 3419 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_alarm | 3420 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_alarm | 3421 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_alarm | 3422 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_alarm | 3423 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_alarm | 3424 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_alarm | 3425 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_alarm | 3426 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_alarm | 3427 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_alarm | 3428 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_alarm | 3429 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_alarm | 3430 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_alarm | 3431 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_alarm | 3432 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_alarm | 3433 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_alarm | 3434 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_alarm | 3435 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_1_serial_number | 10008 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_2_serial_number | 10026 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_3_serial_number | 10044 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_4_serial_number | 10062 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_5_serial_number | 10080 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_6_serial_number | 10098 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_7_serial_number | 10116 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_8_serial_number | 10134 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_9_serial_number | 10152 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_10_serial_number | 10170 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_11_serial_number | 10188 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_12_serial_number | 10206 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_13_serial_number | 10224 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_14_serial_number | 10242 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_15_serial_number | 10260 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_16_serial_number | 10278 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_17_serial_number | 10296 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_18_serial_number | 10314 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_19_serial_number | 10332 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_20_serial_number | 10350 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_21_serial_number | 10368 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_22_serial_number | 10386 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_23_serial_number | 10404 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_24_serial_number | 10422 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_25_serial_number | 10440 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_26_serial_number | 10458 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_27_serial_number | 10476 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_28_serial_number | 10494 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_29_serial_number | 10512 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_30_serial_number | 10530 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_31_serial_number | 10548 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_32_serial_number | 10566 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_33_serial_number | 10584 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_34_serial_number | 10602 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_35_serial_number | 10620 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
battery | Pilot | PBAT600 | Modbus RTU |  | cell_36_serial_number | 10638 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Nominal_Frequency | 2017 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Nominal_Voltage | 2018 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Nominal_Current | 2020 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Normal_Phase_Rotation | 2024 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_A_Voltage | 2038 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_B_Voltage | 2039 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_C_Voltage | 2040 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_N_Voltage | 2041 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_A_Current | 2042 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_B_Current | 2043 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_C_Current | 2044 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Logical_Phase_N_Current | 2045 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Peak_Current_Demand_Over_Last_Year | 2048 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Load_Timer_Setpoint | 2050 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Energy_Delivered_Into_Load | 2700 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Energy_Received_Out_of_Load | 2702 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Energy_Delivered_Received | 2704 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Energy_Delivered_Received_Diff | 2706 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Energy_Delivered | 2708 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Energy_Received | 2710 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Energy_Delivered_Received | 2712 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Energy_Delivered_Received_Diff | 2714 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Energy_Delivered | 2716 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Energy_Received | 2718 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Energy_Delivered_Received | 2720 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Energy_Delivered_Received_Diff | 2722 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Phase_A | 3000 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Phase_B | 3002 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Phase_C | 3004 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Phase_N | 3006 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Phase_G | 3008 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_3_Phase_Average | 3010 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Unbalance_Phase_A | 3012 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Unbalance_Phase_B | 3014 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Unbalance_Phase_C | 3016 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Current_Unbalance_Phase_Worst | 3018 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_A_B | 3020 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_B_C | 3022 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_C_A | 3024 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_L_L_Avg | 3026 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_A_N | 3028 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_B_N | 3030 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_C_N | 3032 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_L_N_Avg | 3034 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_A_B | 3038 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_B_C | 3040 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_C_A | 3042 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_Max_L_L | 3044 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_A_N | 3046 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_B_N | 3048 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_C_N | 3050 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Voltage_Unbalance_Max_L_N | 3052 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Power_Phase_A | 3054 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Power_Phase_B | 3056 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Power_Phase_C | 3058 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Active_Power_Total | 3060 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Power_Phase_A | 3062 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Power_Phase_B | 3064 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Power_Phase_C | 3066 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Reactive_Power_Total | 3068 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Power_Phase_A | 3070 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Power_Phase_B | 3072 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Power_Phase_C | 3074 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Apparent_Power_Total | 3076 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Frequency | 3110 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
power_meter | Schneider | PM5650 | Modbus RTU |  | Temperature | 3132 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Status | 40 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarms | 54 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | CB1 Status | 58 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | CB2 Status | 59 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | CB3 Status | 60 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Generator Alarm | 61 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Logic Locked | 62 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Force Commutation | 63 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Generator Start | 64 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Switching Enabled | 65 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Remote Reset | 66 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Emergency Lock | 67 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V1_voltage | 150 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V2_voltage | 152 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V3_voltage | 154 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V12_voltage | 158 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V23_voltage | 160 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_V31_voltage | 162 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V1_voltage | 164 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V2_voltage | 166 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V3_voltage | 168 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V12_voltage | 172 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V23_voltage | 174 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_V31_voltage | 176 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN1_freq | 250 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | LN2_freq | 252 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarm/Event 1 (newest) | 2000 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarm/Event 2 | 2001 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarm/Event 3 | 2002 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarm/Event 4 | 2003 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Alarm/Event 5 | 2004 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Device Status | 622 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Protection Devices | 626 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | ABB | ATS022 | Modbus RTU |  | Nominal Voltage | 624 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Switch_Position | 1001 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Normal_Source_State | 1003 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Alternate_Source_State | 1005 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Common_Register_1006_Status | 1006 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Common_Register_1007_Status | 1007 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Common_Register_1008_Status | 1008 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Voltage_Unbalance_Rate | 2114 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_VCN | 2112 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Source_Rated_Voltage | 3002 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Source_Rated_Frequency | 3004 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Source_Neutral_Position | 3006 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Enable_Abnormal_Frequency_Transfer | 3010 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SI_Under_Frequency_Dropout_Threshold_Percent | 3011 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SI_Under_Frequency_Pickup_Threshold_Percent | 3013 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Under_Frequency_Dropout_Threshold_Percent | 3015 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Under_Frequency_Pickup_Threshold_Percent | 3017 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Under_Voltage_Dropout_Threshold_Value | 3120 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Under_Voltage_Pickup_Threshold_Value | 3122 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SI_Over_Voltage_Dropout_Threshold_Value | 3124 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SI_Over_Voltage_Pickup_Threshold_Value | 3126 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Over_Voltage_Dropout_Threshold_Value | 3128 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | SII_Over_Voltage_Pickup_Threshold_Value | 3130 | Holding Register | 2 | FLOAT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Genset_Start_Failure_Alarm | 3501 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | External_Power_Supply_Presence | 3503 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Onload_Test_Failure_Alarm | 3505 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Offload_Test_Failure_Alarm | 3504 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Unexpected_Position_Alarm | 3506 | Holding Register | 1 | UINT16 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Total_Transfer_Count | 4030 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Total_Transfer_Failure_Count | 4032 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Too_Fast_Transfer_Counter | 4034 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | Schneider | TA63D4L4004TPE | Modbus RTU |  | Configuration_Changed_Count | 4050 | Holding Register | 2 | UINT32 | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysSwitchName | .1.3.6.1.4.1.171.11.153.1000.1.1.0 | SNMP OID |  | OCTETSTRING | 1 | READ/WRITE | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysHardwareVersion | .1.3.6.1.4.1.171.11.153.1000.1.2.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysFirmwareVersion | .1.3.6.1.4.1.171.11.153.1000.1.3.0 | SNMP OID |  | OCTETSTRING | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysLocationName | .1.3.6.1.4.1.171.11.153.1000.1.5.0 | SNMP OID |  | OCTETSTRING | 1 | READ/WRITE | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysIpAddr | .1.3.6.1.4.1.171.11.153.1000.2.5.0 | SNMP OID |  | IPADDRESS | 1 | READ/WRITE | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysIpSubnetMask | .1.3.6.1.4.1.171.11.153.1000.2.6.0 | SNMP OID |  | IPADDRESS | 1 | READ/WRITE | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysGateway | .1.3.6.1.4.1.171.11.153.1000.2.7.0 | SNMP OID |  | IPADDRESS | 1 | READ/WRITE | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port1 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port2 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port3 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port4 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.4 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port5 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.5 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port6 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.6 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port7 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.7 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port8 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.8 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port9 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.9 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlOperStatus_Port10 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.3.10 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port1 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.1 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port2 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.2 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port3 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.3 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port4 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.4 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port5 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.5 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port6 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.6 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port7 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.7 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port8 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.8 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port9 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.9 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysPortCtrlSpeed_Port10 | .1.3.6.1.4.1.171.11.153.1000.1.13.1.2.10 | SNMP OID |  | INTEGER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port1 | .1.3.6.1.2.1.2.2.1.10.1 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port2 | .1.3.6.1.2.1.2.2.1.10.2 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port3 | .1.3.6.1.2.1.2.2.1.10.3 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port4 | .1.3.6.1.2.1.2.2.1.10.4 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port5 | .1.3.6.1.2.1.2.2.1.10.5 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port6 | .1.3.6.1.2.1.2.2.1.10.6 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port7 | .1.3.6.1.2.1.2.2.1.10.7 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port8 | .1.3.6.1.2.1.2.2.1.10.8 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port9 | .1.3.6.1.2.1.2.2.1.10.9 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInOctets_Port10 | .1.3.6.1.2.1.2.2.1.10.10 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port1 | .1.3.6.1.2.1.2.2.1.16.1 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port2 | .1.3.6.1.2.1.2.2.1.16.2 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port3 | .1.3.6.1.2.1.2.2.1.16.3 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port4 | .1.3.6.1.2.1.2.2.1.16.4 | SNMP OID |  |  | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port5 | .1.3.6.1.2.1.2.2.1.16.5 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port6 | .1.3.6.1.2.1.2.2.1.16.6 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port7 | .1.3.6.1.2.1.2.2.1.16.7 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port8 | .1.3.6.1.2.1.2.2.1.16.8 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port9 | .1.3.6.1.2.1.2.2.1.16.9 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutOctets_Port10 | .1.3.6.1.2.1.2.2.1.16.10 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port1 | .1.3.6.1.2.1.2.2.1.14.1 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port2 | .1.3.6.1.2.1.2.2.1.14.2 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port3 | .1.3.6.1.2.1.2.2.1.14.3 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port4 | .1.3.6.1.2.1.2.2.1.14.4 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port5 | .1.3.6.1.2.1.2.2.1.14.5 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port6 | .1.3.6.1.2.1.2.2.1.14.6 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port7 | .1.3.6.1.2.1.2.2.1.14.7 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port8 | .1.3.6.1.2.1.2.2.1.14.8 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port9 | .1.3.6.1.2.1.2.2.1.14.9 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifInErrors_Port10 | .1.3.6.1.2.1.2.2.1.14.10 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port1 | .1.3.6.1.2.1.2.2.1.20.1 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port2 | .1.3.6.1.2.1.2.2.1.20.2 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port3 | .1.3.6.1.2.1.2.2.1.20.3 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port4 | .1.3.6.1.2.1.2.2.1.20.4 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port5 | .1.3.6.1.2.1.2.2.1.20.5 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port6 | .1.3.6.1.2.1.2.2.1.20.6 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port7 | .1.3.6.1.2.1.2.2.1.20.7 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port8 | .1.3.6.1.2.1.2.2.1.20.8 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port9 | .1.3.6.1.2.1.2.2.1.20.9 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | ifOutErrors_Port10 | .1.3.6.1.2.1.2.2.1.20.10 | SNMP OID |  | COUNTER | 1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
switch | D-Link | DGS-1210-10P | SNMP |  | sysUpTime | .1.3.6.1.2.1.1.3.0 | SNMP OID |  | TICKS | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SHT40 | Modbus RTU | 5 | Temperature | 0 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SHT40 | Modbus RTU | 5 | Humidity | 1 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Renesas | FS3000-1005 | Modbus RTU | 7 | AirVelocity | 0 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SDP810-125 | Modbus RTU | 30 | Pressure | 0 | Holding Register | 1 | INT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SDP810-125 | Modbus RTU | 30 | Temperature | 1 | Holding Register | 1 | INT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SPS30 | Modbus RTU | 4 | PM1_0 | 0 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SPS30 | Modbus RTU | 4 | PM2_5 | 1 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SPS30 | Modbus RTU | 4 | PM4_0 | 2 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SPS30 | Modbus RTU | 4 | PM10_0 | 3 | Holding Register | 1 | UINT16 | 0.01 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | Sensirion | SPS30 | Modbus RTU | 4 | TypicalParticleSize | 4 | Holding Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | STMicroelectronics | LIS3DHTR | Modbus RTU | 3 | Accel_X | 0 | Holding Register | 1 | INT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | STMicroelectronics | LIS3DHTR | Modbus RTU | 3 | Accel_Y | 1 | Holding Register | 1 | INT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
environment | STMicroelectronics | LIS3DHTR | Modbus RTU | 3 | Accel_Z | 2 | Holding Register | 1 | INT16 | 0.001 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
Sensor_RS485 | IOT | Temperature_Sensor_XYMD02 | Modbus RTU |  | temp | 1 | Input Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine
Sensor_RS485 | IOT | Temperature_Sensor_XYMD02 | Modbus RTU |  | hum | 2 | Input Register | 1 | UINT16 | 0.1 | READ ONLY | Copy literal variable and metadata from Device Library; do not redefine

## Modular Variables
Category | Manufacturer | Part Number | Protocol | Variable | GPIO Number | Output Rule
Modular | IOT | DRYCONTACT | Modular | drycontactInput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput7 | 7 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput8 | 8 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput9 | 9 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput10 | 10 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput11 | 11 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput12 | 12 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput13 | 13 | Map actual channel, then expose variable unchanged
Modular | IOT | DRYCONTACT | Modular | drycontactInput14 | 14 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerInput7 | 7 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput1 | 8 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput2 | 9 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput3 | 10 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput4 | 11 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput5 | 12 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput6 | 13 | Map actual channel, then expose variable unchanged
Modular | IOT | OPTOCOUPLER | Modular | optocouplerOutput7 | 14 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput7 | 7 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput8 | 8 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput9 | 9 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput10 | 10 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput11 | 11 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput12 | 12 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput13 | 13 | Map actual channel, then expose variable unchanged
Modular | IOT | GPIO | Modular | gpioInputOutput14 | 14 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput7 | 7 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAY | Modular | relayOutput8 | 8 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | RELAYMINI | Modular | relayMiniOutput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput0 | 0 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput1 | 1 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput2 | 2 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput3 | 3 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput4 | 4 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput5 | 5 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput6 | 6 | Map actual channel, then expose variable unchanged
Modular | IOT | AIO | Modular | analogInputOutput7 | 7 | Map actual channel, then expose variable unchanged
I2COUT | IOT | LM75 | I2Cout | temp |  | Map actual channel, then expose variable unchanged

## Rules and Gaps
Rule / Gap | Required Execution
Source of truth | Device Library protocol input is authoritative. Protocol output consumes only variables successfully read through it.
No manual variable | Do not invent field names, scaling, data type, Modbus register, SNMP OID, enum, or access mode in output.
Unknown device escalation | Stop mapping unknown/non-exact device and confirm with Juarendra (juanrendra@gspe.co.id). Record approval before adding or changing Device Library.
Library mismatch | After Juarendra confirmation, fix/add exact device in Device Library, peer review it, then poll and verify before output mapping.
Inventory scope | Keep every item from 20 ft and 40 ft equipment lists. Record active, failed, optional, on-progress, or missing-topic readiness without deleting it from scope.
Deployment profile | 20 ft and 40 ft are separate deployments. Both use Container base .1.3.6.1.4.1.10000.10.16 and must not run together in one SNMP agent.
Output OID | Use Container product base .1.3.6.1.4.1.10000.10.16; output OID maps to a source variable and never replaces source register/OID.
Write access | All output is READ ONLY except approved Modular Mini Relay and Relay channels. Relay writes require allowlist, interlock, acknowledgement, timeout, read-back, audit, and FAT.
PTU migration | PTU migration from .10.14 to .10.15 is approved and mandatory across seed, runtime, MIB, export, tests, and documentation.
Branding | Use manual-user documentation examples already supplied to Deden and Ikhsal for logo, document number, cover, revision scheme, approver/reviewer, confidentiality, and footer.
Traceability | Document library file path, commit SHA, selectedDevice, source protocol/address/register/OID, MQTT topic, and output OID.
Evidence | Capture protocol input payload and SNMP GET/WALK value for every enabled variable.
20 ft correction | Configuration already has corrected 13 SHT40, 1 FS3000-1005, 1 SDP810-125, and 5 AP8881 mappings.
40 ft | Create instance mapping from equipment list; do not reuse 20 ft mapping when model, protocol, address, or topic differs.

## _lookups
Assignees | Statuses
dedenh842@gmail.com | not_started
ikhsalg@gmail.com | in_progress
juanrendra@gspe.co.id | done